## Disclaimer
The THyGA project's goal was to investigate how the end-use appliances(residential and commercial) would behave when fuelled with H2NG blends, evaluating safety, efficiency, lifetime, and environmental performance. The project consortium also worked on recommendations for supporting standardization activities and mitigation test and actions that would support high scale deployement of H2NG blends for new and existing appliances. The project published 18 public reports, and organized several workshops, all available on the website https://thyga-project.eu/ To support the objectives of the European Commission and the Clean Hydrogen Partnership towards knowledge sharing, the THyGA project also published some OpenDatasets on the website: https://thyga-project.eu/category/open-access-data/
This Excel sheets was used to summarize the data from all the tesing per appliance segment -The THyGA project advises the user to read the test protocol and the test results reports before using this calculation sheets -The THyGA project will not be responsible for mis-use of the Excel sheet or bad implementation of the results
This project has received funding from the Fuel Cells and Hydrogen 2 Joint Undertaking (now Clean Hydrogen Partnership) under Grant Agreement No 874983. This Joint Undertaking receives support from the European Union’s Horizon 2020 Research and Innovation program, Hydrogen Europe and Hydrogen Europe Research.
Instructions
do not touch column A forom each sheet
the only formula are used to produce the diffeent figures of report D3.8. you cna produce them using the red cell with diferent KPIs

## List (hidden)
KPI | Y axis
Wobbe index | Wobbe index (Ws) (MJ/m3)
Efficiency (Hi) | Efficiency (% in Hi)
Qtest (input) | Power (kW)
Air Excess (Lambda) | Air excess (-)
CO emissions | CO emissions (ppm)
NOx emissions | NOx emissions (ppm)
CO2 emissions | CO2 emissions (%)
O2 emissions | O2 emissions (%)
Flue gases temperatures | Temperature (°C)
Unburnt UHC emissions | Unburnt (ppm)
Unburnt H2 emissions | Unburnt (ppm)

## THyGA segments
THyGA Segment | Type of appliance | Category | Burner type | Standard | Total Appliance Population
101 | BOILERS | Open flued (former EN 297) | Partial premix/conv (atmos. & fanned) | EN 15502 | 13.588
102 |  |  | Low NOx technology burners |  | 2.012
103 |  |  | Full premix |  | 152
104 |  | Room-sealed (former EN 483) | Partial premix/conv (atmos. & fanned) |  | 25.333
105 |  |  | Low NOx technology burners |  | 1.972
106 |  |  | Full premix |  | 1.781
107 |  | Condensing boiler (former EN 677) | Partial premix fanned |  | 2.920
108 |  |  | Full premix (including CCB) |  | 56.492
109 |  | Forced-draught / Jet burner boiler (former EN 303-3) | Jet burner |  | 1.129
201 | WATER HEATERS | Instantaneous open flued | Partial premix/atmos | EN 26 | 10.462
202 |  | Instantaneous room-sealed | Partial premix/fanned |  | 4.484
203 |  | Storage open flued | Partial premix/atmos | EN 89 | 2.185
204 |  | Storage room-sealed | Partial premix/fanned |  | 936
501 | Space Heaters | Independent gas-fired convection heaters type B | heating & decoration | EN 613 | 4.678
502 |  | Independent gas-fired convection heaters type C | heating & decoration, balanced | EN 613 | 1.839
503 |  | Decorative fuel-effect gas appliance/burner | heating & decoration | EN 13278 + EN 509 | 2.529
504 |  | Independent gas-fired flueless space heaters | heating & decoration | EN 14829 | 98
601 | CHP | Stirling Engines | heating & electricity production | EN 50465 | 15
602 |  | Internal Combustion Engine |  |  | 41
603 |  | Micro Gas Turbine |  |  | 1
604 |  | PEM FC |  |  | 5
605 |  | SO FC |  |  | 3
701 | HP | Engine HP | Heating | EN 16905 | 48
702 |  | Adsorption |  | EN 12309 | 3
703 |  | Absorption |  |  | 9
801 | OTHER | Commercial Dryers |  | EN 12752-1 and -2 | unknown
802 |  | Infrared Radiant Heaters (former EN 416-1) | non-domestic, tube radiant heaters | EN 416 | 375
803 |  | Infrared Radiant Heaters (former EN 419-1) | non-domestic, luminous radiant heaters | EN 419 | 375
804 |  | Infrared Radiant Heaters (former EN 777-1) | non-domestic, tube radiant heaters | EN 416 | 375
804bis |  | Radiant strip | with fan driven burners and recirculation fans | EN 17082 | 375
805 |  | Air heaters (former EN 1020) | non-domestic, forced convection, fan, <300kW | EN 17082 | 495
806 |  | Air heaters (former EN 525) | non-domestic, forced convection, <300kW | EN 17082 | 495
807 |  | Air Heaters <70kW (former EN778) | Ducted warm air; forced convection air heaters | EN 1518 | 510
808 |  | domestic washing machines |  | EN 1518 | 2
809 |  | domestic dryers |  | EN 12752-1 and -2 | 2
301 | COOKERS | Surface burner (cooktops) with atmospheric burner or "Venturi" burner (vertical venturi burner) | Single ring | EN 30-x | 13.030
302 |  |  | Single crown |  | 16.287
303 |  |  | Multi ring (mainly double or triple ring) |  | 3.257
304 |  | Surface burner (cooktops) with partially premix burner (long horizontal venturi) | Single ring |  | 541
305 |  |  | Single crown |  | 676
306 |  |  | Multi ring (mainly double or triple ring) |  | 135
307 |  | Cavity burner "tubular" (ovens, freestanding ranges) | Atmospheric burner |  | 2.697
308 |  |  | "Venturi" burner |  | 1.156
309 |  |  | Partially premixed |  | 27.712
310 |  | Cavity burner "metal sheet" (ovens, freestanding ranges) | Atmospheric burner |  | 9.139
311 |  |  | "Venturi" burner |  | 3.917
312 |  |  | Partially premixed |  | 14.658
401 | CATERING | Open burners and wok burners | Circular burner with vertical slots | EN 203-2-1 | 120
402 |  |  | Circular burner with holes |  | 120
403 |  | Mixed ovens | Draught burners | EN 203-2-2 | 120
404 |  | Ovens | Tubular or circular burners |  | 120
405 |  | Boiling pans / pasta cookers | Microperforated burner | EN 203-2-3 EN 203-2-11 | 120
406 |  | Fryers | Premix burner | EN 203-2-4 | 120
407 |  | Salamanders / Rotisseries | Ceramic or blue flame burners | EN 203-2-7 | 120
408 |  | Brat pans | multi-ramp tubular slot burners | EN 203-2-8 | 120
409 |  | Covered burners (griddles, solid tops, pancake cookers) | Tubular burner or multi-ramp tubular burner | EN 203-2-9 | 120
410 |  | Barbecues | Chargrill with burner tubes w/ holes on top | EN 203-2-10 | 120

## Seg100a Boiler Premix
Do not touch this colum | THyGA Segment 100a - Boiler Premix |  |  | THyGA Test data - Values | [19 empty] | Graph for the indicator (KPI): |  |  |  |  | CO emissions
|  |  |  | GW01V04 | AP02V03 | D5v02 | D4v03 | D6 | GW05V04 | GW06V03 | GW07V02 | GW08V02 | GW10V02 | GW11V02 | GW17 | EB01V04 | GW13V02 | EN01v01 | EN02v01 | GA11V03 | EN21 | GW21 | GW23 |  | GW01V04 | AP02V03 | D5v02 | D4v03 | D6 | GW05V04 | GW06V03 | GW07V02 | GW08V02 | GW10V02 | GW11V02 | GW17 | EB01V04 | GW13V02 | EN01v01 | EN02v01 | GA11V03 | EN21 |  |  | GW21 | GW23
| SEGMENT Nr |  |  | GW1_SEGM_108 | A+_SEGM_108 | D5_SEGM_108 | D4_SEGM_108 | D6_SEGM_108 | GW5_SEGM_108 | GW06_SEGM_108 | GW07_SEGM_108 | GW08_SEGM_108 | GW10_SEGM_108 | GW11_SEGM_108 | GWI_17_SEGM_108 | EB01_SEGM_108 |  | EN01_SEGM_108 | EN02_SEGM_106 | GA11_SEGM_108
|  | Report test lab code |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 106 | 108 | 108 | 108 | 108 | Qmax | Graph title | THyGA Segment 100a - Boiler Premix - CO emissions at Qmax | [5 empty] | Y axis | CO emissions (ppm)
|  | Appliance type code (B, CH, CO, F, WH,O) (*) |  | GW1 | A+ | D5 | D4 | D6 | GW5 | GWI06 | GW07 | GW08 | GW10 | GWI11 | GWI_17 | EB01 | GW13 | EN01 | EN02 | GA11 | EN21 | GW21 | GWI23 | %H2 | GW01 | AP02 | D5v0 | D4v0 | D6 | GW05 | GW06 | GW07 | GW08 | GW10 | GW11 | GW17 | EB01 | GW13 | EN01 | EN02 | GA11 | EN21 |  |  | GW21 | GW23
|  | Appliance type |  | B | B | EN 15502 Gas-fired heating boiler | B | EN 15502 Gas-fired heating boiler | B | B | B | B | B | B | B | Condensing Boiler (B) | B | CH | CH | B | CH | B | B | 0 | 32.37 | 109.2249 | 213.9065 | 82.5967 | 59.4573 | 57.2 | 47.3 | 27.1 | 57.1 | 66.1 | 23.2 | 73.5 | 138.9934 | 61.8 | 64.8819 | 2.2595 | 59.103 | 72.9242 | #N/A | #N/A | 53.2 | 44.8
[18 empty] | 0 | 0 |  |  |  |  | 10 | 25.7645 | #N/A | #N/A | 61.8084 | #N/A | 41.7 | 37.5 | 19.8 | 45.8 | 57.2 | 14.6 | 58 | 101.3611 | 47.6 | #N/A | 1.2671 | #N/A | #N/A | #N/A | #N/A | 39.2 | 35.1
|  | Burner type |  | full premixed | Full premix | Premix | Premix | Premix | full premixed | full premixed | fully premixed | 30% H2 certified burner | full premixed | full premixed | Condensing Boiler | Furipat steel cylindrical | fully premixed | Full premix | Condensing Boiler | premix | Full premix | Full premixed | Full premix | 20 | #N/A | #N/A | #N/A | 43.6549 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 73.7102 | #N/A | #N/A | 2.7243 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | For cooker hobs: burner tested? |  |  |  | na | na | na | [9 empty] | 0 | 0 |  |  |  |  | 23 | 21.86 | 55.2958 | 108.2007 | 37.4301 | #N/A | 33.2 | 27.5 | 12.7 | 35.2 | 40.3 | 13.5 | 54.7 | 66.8385 | 33.5 | 35.2817 | 1.962 | 28.6136 | 39.9967 | #N/A | #N/A | 29.2 | 25.5
|  | Modulating burner (Y/N) |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | 30 | 19.88 | #N/A | #N/A | 29.5921 | #N/A | 31.8 | 23.5 | 11.8 | 31.8 | 31.9 | 16.4 | 59.9 | 54.3137 | 27.3 | #N/A | 1.8334 | #N/A | #N/A | #N/A | #N/A | 26.1 | 21.5
|  | Pressure regulator (Y/N) |  | Y |  | Y | Y | Y | N | Y | N | Y | N | N | N | Y | Y | 0 | 0 | Y |  | N | N | 40 | 17.05 | 22.3632 | 53.0034 | 20.822 | 10.413 | 28.3 | 18.7 | 8.9 | 28.1 | 22.4 | 22 | 83.4 | 40.4607 | 19.9 | 20.4079 | 1.8061 | 15.0813 | 25.4217 | #N/A | #N/A | 22.4 | 17.2
|  | Can the appliance be adjusted (Y/N) |  | N | Y | Y | Y | Y | N | N | N | Y | N | N | N | Y | N | Y | Y | Y | N | N | N | 50 | #N/A | 14.3293 | #N/A | 13.831 | #N/A | 24.7 | #N/A | 6.7 | 25 | 15.7 | 28.4 | 121.1 | #N/A | 15.5 | #N/A | 1.9322 | #N/A | #N/A | #N/A | #N/A | 19.6 | 13.9
|  | Is the appliance equiped with a combustion control (Y/N) |  | Y |  | Y | Yes | Y | Y | N | N | Y | Y |  | N | Y | Y | N | N | n | Y | Y | Y | 60 | #N/A | 9.5507 | #N/A | 10.9936 | #N/A | 19.3 | #N/A | 5.1 | 22.2 | 11.6 | 30.6 | 119.6 | #N/A | 12.5 | #N/A | 6.9895 | #N/A | #N/A | #N/A | #N/A | 17.8 | 10.4
|  | If the appliance can be adjusted. Instructions: |  |  | Y (8,8%CO2) | See note at the "Appliance" sheet | CO2 shall be adjusted to 9% with G20 | See note ( green area right below) | [7 empty] | According to the manufacturer guidelines, CO2 and O2 values are adjusted with respect to the natural gas. |  | Y | 0 | Y | Y
|  | If Yes what technology is used? |  |  |  | Ionisation | Pneumatic. Gas volume modified as a function of the air flow. Not depending on gas quality | Ionisation | [7 empty] | Pneumatic Gas-Air system |  | 0 | 0 |  | All gas sensor CO sensor
|  | Max. power input (net) [kW] |  | 24 | 22 | 20.8 | 20 | 22 | 20.5 | 15.3 | 22 | 22.5 | 32 | 20 | 32 | 30 | 3.2 | 12.5 | 41.6 | 17.8 | 30.3 | 20.4 | 15.2 | Qmin | Graph title | THyGA Segment 100a - Boiler Premix - CO emissions at Qmin | [5 empty] | Y axis | CO emissions (ppm)
|  | Min. power input (net) [kW] |  | 6.9 | 2.5 | 4.3 | 4.8 | 2.5 | 6 | 4.5 | 6 | / | 2.5 | 2.9 | 5.1 | 4.8 | 25 | 2.1 | 8.3 | 6.1 | 3.3 | 4.4 | 4.5 | %H2 | GW01 | AP02 | D5v0 | D4v0 | D6 | GW05 | GW06 | GW07 | GW08 | GW10 | GW11 | GW17 | EB01 | GW13 | EN01 | EN02 | GA11 | EN21 |  |  | GW21 | GW23
|  | Flue type |  |  | Type C | tbd | na | Coaxial | [7 empty] | 60/100 |  | C | C | B23 | C |  |  | 0 | 20.3238 | 14.1062 | 18.1647 | 0.76676 | 1.2672 | 9.9 | 19.3 | 5.9 | 52.7 | 7.4 | 5.3 | 7.3 | 15.0387 | 11.5 | 5.4041 | 22.0245 | 12.9877 | 12.4266 | #N/A | #N/A | 12.72 | 22.5
|  | Flue lenght |  |  | concetric 1m | tbd | na | 1 m | 1m | 1m | 1m | 1m | 1m | 1m | 1 m | 0,8 m | 1m | 1M | 1m | 1 | 1M | 1m | 1m | 10 | 19.0354 | #N/A | #N/A | 0.78802 | #N/A | 8.7 | 17.3 | 5.4 | 53.5 | 6.7 | 5 | 6.9 | 14.8236 | 12 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10.57 | 21.1
|  | Applicable standard(s) |  |  | EN15502 | EN 15502 | EN 15502 | EN 15502 | [7 empty] | EN 15502 |  | 0 | EN 15502-1 | EN 15502 |  |  |  | 20 | #N/A | #N/A | #N/A | 0.20916 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 13.9938 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Gas category |  | II2ELL | II2H3P | II 2H3B/P | II 2H3B/P | II 2H3B/P | II2N3P | II2N | II2ELL 3P | II2L3P | II2N3P | 2N3P | II2H3P | 2Es - G20 - 20 mbar | II2N3P | II2Esi3P | II2Esi3P I2Esi | I2E(S) | II2H3P | II2N3P | I2H | 23 | 18.0094 | 2.9342 | 14.4561 | 1.2291 | 1.1754 | 7.8 | 16.7 | 4.7 | 48.2 | 5.8 | 4.8 | 6.3 | 14.2628 | 11.1 | 5.4331 | 14.9618 | 6.2721 | 15.6525 | #N/A | #N/A | 9.24 | 19.8
|  | Origin of the appliance |  | old used by GWI many times | market (brand new) | Sent by the manufacturer | Sent by the manufacturer | Sent by the manufacturer | new/owned by GWI | new | old/used by GWI MRU | new | new from another project | new | New | Italy | new | Atlantic | 0 | Already uses for other project | Vaillant |  | new | 30 | 17.4486 | #N/A | #N/A | 0.71717 | #N/A | 7.4 | 16.9 | 4.2 | 51.2 | 5.1 | 4.7 | 5.9 | 14.5528 | 9.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 8.5 | 19.2
|  | Manufacture year |  |  | 2021 | 28th of July 2020 | 2020 | Need information from manufacturer | 2020 |  | 2009 | 2021 |  |  | 2013 | 2020 | 2022 | 2021 | 2020 | 2016 | 2022 | new |  | 40 | 15.8608 | 3.3825 | 12.8435 | 0.34545 | 0.62694 | 7 | 17.5 | 3.6 | 51.2 | 4.8 | 4.6 | 5.3 | 15.3233 | 7.1 | 6.8533 | 22.0557 | 2.6437 | 10.6658 | #N/A | #N/A | 7.69 | 18.5
[24 empty] | 50 | #N/A | 2.9756 | #N/A | 0.17826 | #N/A | 6.3 | #N/A | 3 | 50.9 | 4.4 | #N/A | #N/A | #N/A | 5.8 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.14 | 18.2
[24 empty] | 60 | #N/A | 1.5807 | #N/A | 1.2727 | #N/A | #N/A | #N/A | 2.4 | #N/A | 3.8 | #N/A | #N/A | #N/A | 4.8 | #N/A | 23.8546 | #N/A | #N/A | #N/A | #N/A | #N/A | 17.1
QMAX
H2
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | 10.1 | #N/A | #N/A | 9.2771 | #N/A | 10.2 | 10.1 | 9.9 | 10.5 | 9.9 | 10 | 10.4 | 10 | 9.9 | #N/A | 8.36 | #N/A | #N/A | 10.2 | 10.2
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | 18.7171 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20 | #N/A | #N/A | 17.95 | #N/A | #N/A | #N/A | #N/A
H2 - 23% |  |  | 23 | 23.5 | 19.2 | 20.9 | 21.4689 | 24.1685 | 23.3 | 23.4 | 23.3 | 23.9 | 23 | 23 | 22.7 | 23 | 23.1 | 23.04 | 21.39 | 23 | 23.0717 | 23.1 | 22.9
H2 - 30% |  |  | 30 | 30.6 | #N/A | #N/A | 28.2752 | #N/A | 30.2 | 30.5 | 30.4 | 31 | 30.1 | 30 | 30.4 | 30 | 30.1 | #N/A | 27.96 | #N/A | #N/A | 30.2 | 29.8
H2 - 40% |  |  | 40 | 40.4 | 39.2 | 38.4 | 38.3705 | 41.494 | 40.2 | 40.4 | 40.3 | 40.8 | 40.1 | 40 | 40.1 | 40 | 40 | 40.09 | 38.99 | 40 | 40.1062 | 40.1 | 39.9
H2 - 50% |  |  | 50 | #N/A | 48 | #N/A | #N/A | #N/A | 50.2 | #N/A | 50.2 | 50.6 | 50 | 50 | 49.9 | #N/A | 50.3 | #N/A | 48.82 | #N/A | #N/A | 50.3 | 50.4
H2 - 60% |  |  | 60 | #N/A | 57.6 | #N/A | 60.3105 | #N/A | 60 | #N/A | 60 | 60 | 59.9 | 60 | 59.9 | #N/A | 60.2 | #N/A | 60.1 | #N/A | #N/A | 60.1 | 60
|  | Wobbe index | [MJ/m³]
Wobbe index - 0% |  | %H2 in test gas | 0 | 53.4706 | 50.6063 | 53.4706 | 50.5367 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6038 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063
Wobbe index - 10% |  |  | 10 | 52.1605 | #N/A | #N/A | 49.3992 | #N/A | 49.354 | 49.3664 | 49.2612 | 49.3171 | 49.391 | 49.4156 | 49.3294 | 49.3787 | 49.391 | #N/A | 49.5805 | 50.6063 | #N/A | 49.354 | 49.354
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | 48.235 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 48.1467 | #N/A | #N/A | 48.3992 | #N/A | #N/A | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | 50.4168 | 48.2452 | 50.7547 | 47.8947 | 47.6526 | 47.7407 | 47.7284 | 47.714 | 47.667 | 47.7776 | 47.7776 | 47.8145 | 47.7776 | 47.7653 | 47.7727 | 47.9756 | 47.7776 | 47.7688 | 47.7653 | 47.7899
Wobbe index - 30% |  |  | 30 | 49.4984 | #N/A | #N/A | 47.0583 | #N/A | 46.8956 | 46.859 | 46.8441 | 46.7981 | 46.9078 | 46.92 | 46.8712 | 46.92 | 46.9078 | #N/A | 47.1692 | #N/A | #N/A | 46.8956 | 46.9444
Wobbe index - 40% |  |  | 40 | 48.2518 | 45.8096 | 48.5032 | 45.8356 | 45.482 | 45.6907 | 45.667 | 45.6513 | 45.6197 | 45.7026 | 45.7145 | 45.7026 | 45.7145 | 45.7145 | 45.7038 | 45.8346 | 45.7145 | 45.7019 | 45.7026 | 45.7263
Wobbe index - 50% |  |  | 50 | #N/A | 44.7833 | #N/A | 44.6237 | #N/A | 44.5354 | #N/A | 44.5633 | 44.4909 | 44.5578 | 44.5578 | 44.569 | #N/A | 44.5243 | #N/A | 44.6904 | #N/A | #N/A | 44.5243 | 44.5131
Wobbe index - 60% |  |  | 60 | #N/A | 43.7408 | #N/A | 43.4701 | #N/A | 43.4999 | #N/A | 43.5552 | 43.4999 | 43.5097 | 43.5097 | 43.5097 | #N/A | 43.4803 | #N/A | 43.4901 | #N/A | #N/A | 43.4901 | 43.4999
|  | Efficiency (Hi) | % on Hi
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 100.0514 | 96.7 | 102.5194 | 102.1702 | 102.0783 | 101.4557 | 101.1489 | 101.8142 | 102.1 | 99.8 | 99 | 103 | #N/A | 97.8 | 105.8921 | 103.5043 | 101.4493 | 107.0611 | 101.3 | 100.6
Efficiency (Hi) - 10% |  |  | 10 | 98.8328 | #N/A | #N/A | 101.7141 | #N/A | 101.3621 | 100.9299 | 102.5063 | 102.3 | 99.9 | 98.5 | 103.3 | #N/A | 97.6 | #N/A | 103.653 | #N/A | #N/A | 101.4 | 100.6
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | 101.5686 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 103.4779 | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | 100.1766 | 96.9 | 101.5418 | 101.2253 | 102.209 | 101.2284 | 101.4124 | 102.6332 | 102.8 | 100.4 | 98.7 | 103 | #N/A | 98 | 105.5934 | 103.7733 | 103.3245 | 107.0614 | 101.6 | 101
Efficiency (Hi) - 30% |  |  | 30 | 100.8935 | #N/A | #N/A | 101.2885 | #N/A | 101.5781 | 101.7245 | 103.0045 | 103.1 | 100.7 | 99 | 103.8 | #N/A | 98.1 | #N/A | 103.7692 | #N/A | #N/A | 102 | 101.4
Efficiency (Hi) - 40% |  |  | 40 | 101.4696 | 95 | 101.1633 | 101.3605 | 102.5057 | 101.7775 | 102.0763 | 103.4241 | 103.5 | 101.2 | 99.4 | 103.8 | #N/A | 98.4 | 105.0178 | 103.695 | 104.1152 | 107.1419 | 102.4 | 101.9
Efficiency (Hi) - 50% |  |  | 50 | #N/A | 93.2 | #N/A | 101.3976 | #N/A | 102.3016 | #N/A | 103.8512 | 104.5 | 101.7 | 100 | 104 | #N/A | 99.5 | #N/A | 103.3196 | #N/A | #N/A | 103.6 | 103.3
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 102.8042 | #N/A | 104.6 | 105 | 102.2 | 100.1 | 104.7 | #N/A | #N/A | #N/A | 105.8278 | #N/A | #N/A | 104.5 | 104
|  | CO emissions | ppm
CO emissions - 0% |  | %H2 in test gas | 0 | 32.37 | 109.2249 | 213.9065 | 82.5967 | 59.4573 | 57.2 | 47.3 | 27.1 | 57.1 | 66.1 | 23.2 | 73.5 | 138.9934 | 61.8 | 64.8819 | 2.2595 | 59.103 | 72.9242 | 53.2 | 44.8
CO emissions - 10% |  |  | 10 | 25.7645 | #N/A | #N/A | 61.8084 | #N/A | 41.7 | 37.5 | 19.8 | 45.8 | 57.2 | 14.6 | 58 | 101.3611 | 47.6 | #N/A | 1.2671 | #N/A | #N/A | 39.2 | 35.1
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 43.6549 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 73.7102 | #N/A | #N/A | 2.7243 | #N/A | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | 21.86 | 55.2958 | 108.2007 | 37.4301 | #N/A | 33.2 | 27.5 | 12.7 | 35.2 | 40.3 | 13.5 | 54.7 | 66.8385 | 33.5 | 35.2817 | 1.962 | 28.6136 | 39.9967 | 29.2 | 25.5
CO emissions - 30% |  |  | 30 | 19.88 | #N/A | #N/A | 29.5921 | #N/A | 31.8 | 23.5 | 11.8 | 31.8 | 31.9 | 16.4 | 59.9 | 54.3137 | 27.3 | #N/A | 1.8334 | #N/A | #N/A | 26.1 | 21.5
CO emissions - 40% |  |  | 40 | 17.05 | 22.3632 | 53.0034 | 20.822 | 10.413 | 28.3 | 18.7 | 8.9 | 28.1 | 22.4 | 22 | 83.4 | 40.4607 | 19.9 | 20.4079 | 1.8061 | 15.0813 | 25.4217 | 22.4 | 17.2
CO emissions - 50% |  |  | 50 | #N/A | 14.3293 | #N/A | 13.831 | #N/A | 24.7 | #N/A | 6.7 | 25 | 15.7 | 28.4 | 121.1 | #N/A | 15.5 | #N/A | 1.9322 | #N/A | #N/A | 19.6 | 13.9
CO emissions - 60% |  |  | 60 | #N/A | 9.5507 | #N/A | 10.9936 | #N/A | 19.3 | #N/A | 5.1 | 22.2 | 11.6 | 30.6 | 119.6 | #N/A | 12.5 | #N/A | 6.9895 | #N/A | #N/A | 17.8 | 10.4
|  | NOx emissions | ppm
NOx emissions - 0% |  | %H2 in test gas | 0 | 18.33 | 16.7868 | 37.3584 | 27.5587 | 17.6851 | 12.45 | 32.6 | 48.1 | 35.1 | 13.9 | 15 | 15.2 | 11.2872 | 11.5 | 25.6669 | 46.4883 | 31.1269 | 28.9725 | 13 | 31.3
NOx emissions - 10% |  |  | 10 | 13.106 | #N/A | #N/A | 21.3074 | #N/A | 8.38 | 24.8 | 35.7 | 26.5 | 13.4 | 8.1 | 11 | 9.182 | 10.2 | #N/A | 34.1045 | #N/A | #N/A | 10 | 24.5
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 16.7775 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.9315 | #N/A | #N/A | 25.0192 | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | 9.9 | 10.889 | 23.6166 | 15.302 | #N/A | 5.32 | 17.6 | 23.7 | 18 | 10.8 | 4.4 | 7.1 | 7.5098 | 8.5 | 12.8116 | 21.0312 | 15.5796 | 16.9301 | 8.1 | 17.3
NOx emissions - 30% |  |  | 30 | 8.39 | #N/A | #N/A | 12.671 | #N/A | 4.33 | 14.4 | 16.8 | 14.8 | 9.4 | 3.4 | 5.8 | 6.2094 | 7.5 | #N/A | 17.9006 | #N/A | #N/A | 7.6 | 14.4
NOx emissions - 40% |  |  | 40 | 6.66 | 7.0284 | 14.4369 | 10.2762 | 4.0416 | 3.49 | 11 | 11.7 | 11.4 | 7.5 | 2.6 | 4.2 | 5.5326 | 6.3 | 8.6933 | 11.9903 | 9.3608 | 11.5065 | 7.1 | 11.1
NOx emissions - 50% |  |  | 50 | #N/A | 5.7317 | #N/A | 7.7282 | #N/A | 3.13 | #N/A | 7.8 | 9 | 6.1 | 2.1 | 3 | #N/A | 5.1 | #N/A | 8.9425 | #N/A | #N/A | 7.1 | 8.6
NOx emissions - 60% |  |  | 60 | #N/A | 4.9664 | #N/A | 7.6334 | #N/A | 3.02 | #N/A | 5.3 | 7.4 | 5.1 | 1.7 | 2.4 | #N/A | 4.3 | #N/A | 6.6277 | #N/A | #N/A | 7.2 | 6.7
|  | Qtest (input) | kW
Qtest (input) - 0% |  | %H2 in test gas | 0 | 24.2675 | 20.8248 | 20.4318 | 20.0643 | 20.9906 | 20.5607 | 15.3734 | 21.5982 | 21.7868 | 30.8411 | 18.9573 | 30.6524 | 30.9164 | 22.6356 | 11.5917 | 40.8099 | 18.1095 | 23.1571 | 20.9568 | 15.0999
Qtest (input) - 10% |  |  | 10 | 23.8686 | #N/A | #N/A | 19.4067 | #N/A | 20.1456 | 14.9014 | 21.1304 | 21.1488 | 30.4622 | 17.7597 | 29.3858 | 29.5903 | 22.298 | #N/A | 39.4296 | #N/A | #N/A | 20.2332 | 14.6099
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | 18.8698 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.7933 | #N/A | #N/A | 38.0081 | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | 22.63 | 19.4013 | 19.5639 | 18.9193 | 18.765 | 20.1327 | 14.1994 | 20.2664 | 20.1889 | 29.2853 | 16.4631 | 27.8509 | 28.6793 | 21.5107 | 10.828 | 37.3699 | 16.7006 | 21.779 | 19.6048 | 13.9895
Qtest (input) - 30% |  |  | 30 | 22.043 | #N/A | #N/A | 18.3313 | #N/A | 20.0142 | 13.802 | 19.805 | 19.6506 | 28.5957 | 15.8757 | 26.8115 | 28.074 | 21 | #N/A | 36.8028 | #N/A | #N/A | 19.3222 | 13.619
Qtest (input) - 40% |  |  | 40 | 21.3463 | 18.0953 | 18.459 | 17.7265 | 17.2431 | 19.9356 | 13.2646 | 19.0091 | 19.0104 | 27.4212 | 15.2186 | 25.5207 | 26.8278 | 20.2462 | 10.2299 | 35.4308 | 15.7146 | 20.7027 | 19.0659 | 13.0368
Qtest (input) - 50% |  |  | 50 | #N/A | 19.2006 | #N/A | 17.0555 | #N/A | 19.8335 | #N/A | 18.2087 | 18.1633 | 26.2563 | 14.5391 | 24.1351 | #N/A | 19.323 | #N/A | 34.1852 | #N/A | #N/A | 18.8582 | 12.3692
Qtest (input) - 60% |  |  | 60 | #N/A | 18.4047 | #N/A | 16.4465 | #N/A | 19.7657 | #N/A | 17.4713 | 17.5209 | 25.1618 | 14.0336 | 22.9142 | #N/A | 18.5165 | #N/A | 32.4206 | #N/A | #N/A | 18.7794 | 11.8211
|  | Flue gases temperatures | [°C]
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 55.74 | #N/A | 55.9735 | 70.3521 | 60.5189 | 59.3 | 53.9 | 50.6 | 48.2 | 62.8 | 54.8 | 49.6 | 56.0821 | 73.6 | 66.485 | 56.72 | 48.79 | 54.6 | 55.6 | 52.2
Flue gases temperatures - 10% |  |  | 10 | 56.4 | #N/A | #N/A | 68.9702 | #N/A | 59.5 | 53.6 | 50.5 | 48.3 | 62 | 54.1 | 49.4 | 55.5876 | 74.6 | #N/A | 56.63 | #N/A | #N/A | 55.5 | 52
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | 68.3888 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 55.3286 | #N/A | #N/A | 55.63 | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | 55.03 | #N/A | 55.2051 | 68.6128 | 58.9366 | 60.4 | 53.3 | 50.4 | 47.7 | 61.8 | 53.3 | 49.1 | 54.8981 | 74.8 | 65.6963 | 56 | 48.64 | 53.61 | 55.2 | 51.7
Flue gases temperatures - 30% |  |  | 30 | 54.79 | #N/A | #N/A | 67.6579 | #N/A | 59.9 | 53.1 | 50.3 | 47.5 | 59.2 | 53 | 48.8 | 53.7242 | 75.5 | #N/A | 55.3 | #N/A | #N/A | 55.1 | 51.5
Flue gases temperatures - 40% |  |  | 40 | 54.56 | #N/A | 54.445 | 66.8147 | 57.6098 | 59 | 52.8 | 50 | 47.6 | 59.6 | 52.7 | 48.4 | 53.5417 | 75 | 65.273 | 55.01 | 48.6 | 53.13 | 55 | 51.3
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | 65.1933 | #N/A | 58.7 | #N/A | 49.6 | 47.6 | 57.2 | 52.5 | 48 | #N/A | 75.6 | #N/A | 54.96 | #N/A | #N/A | 55.1 | 51.1
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 58.9 | #N/A | 49.3 | 46.8 | 57 | 51.7 | 47.6 | #N/A | 74.2 | #N/A | 56 | #N/A | #N/A | 55.1 | 50.9
|  | CO2 emissions | [%]
CO2 emissions - 0% |  | %H2 in test gas | 0 | 8.2 | 8.95 | 9.3485 | 9.0653 | 8.3965 | 8.28 | 9.07 | 9.43 | 9.17 | 8.31 | 8.5 | 8.63 | 8.4867 | 8.19 | 9.1644 | 8.962 | 9.16 | 9.09 | 8.32 | 9.15
CO2 emissions - 10% |  |  | 10 | 7.5728 | #N/A | #N/A | 8.3361 | #N/A | 7.59 | 8.51 | 8.83 | 8.6 | 7.98 | 7.56 | 8.01 | 7.9401 | 7.78 | #N/A | 8.4633 | #N/A | #N/A | 7.76 | 8.57
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 7.8191 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.3986 | #N/A | #N/A | 7.988 | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | 6.98 | 7.8 | 8.1272 | 7.7459 | 6.906 | 6.75 | 7.75 | 8 | 7.8 | 7.34 | 6.58 | 7.14 | 7.2336 | 7.15 | 7.8409 | 7.779 | 7.85 | 7.97 | 7.14 | 7.78
CO2 emissions - 30% |  |  | 30 | 6.63 | #N/A | #N/A | 7.2503 | #N/A | 6.35 | 7.33 | 7.53 | 7.35 | 6.94 | 6.13 | 6.69 | 6.8216 | 6.7 | #N/A | 7.427 | #N/A | #N/A | 6.83 | 7.35
CO2 emissions - 40% |  |  | 40 | 6.08 | 6.38 | 6.9899 | 6.6594 | 5.778 | 5.81 | 6.69 | 6.84 | 6.68 | 6.3 | 5.53 | 5.99 | 6.2117 | 6.08 | 6.9101 | 6.722 | 6.83 | 6.99 | 6.4 | 6.7
CO2 emissions - 50% |  |  | 50 | #N/A | 5.4 | #N/A | 5.9677 | #N/A | 5.28 | #N/A | 6.08 | 6 | 5.61 | 4.94 | 5.23 | #N/A | 5.41 | #N/A | 6.023 | #N/A | #N/A | 5.95 | 6
CO2 emissions - 60% |  |  | 60 | #N/A | 4.69 | #N/A | 5.3225 | #N/A | 4.73 | #N/A | 5.26 | 5.28 | 4.88 | 4.26 | 4.51 | #N/A | 4.66 | #N/A | 5.3142 | #N/A | #N/A | 5.41 | 5.23
|  | O2 emissions | [%]
O2 emissions - 0% |  | %H2 in test gas | 0 | 5.95 | 5.95 | 4.145 | 4.7723 | 5.9861 | 5.94 | 4.6 | 4.13 | 4.29 | 6.03 | 5.58 | 5.76 | 5.4557 | 6.01 | 4.7795 | 4.6812 | #N/A | 5.72 | 6.03 | 4.37
O2 emissions - 10% |  |  | 10 | 6.7201 | #N/A | #N/A | 5.377 | #N/A | 6.77 | 5.14 | 4.75 | 4.87 | 6.27 | 6.84 | 6.5 | 6.0521 | 6.34 | #N/A | 5.2805 | #N/A | #N/A | 6.64 | 4.98
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 5.9859 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.6244 | #N/A | #N/A | 6.045 | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | 7.24 | 7.05 | 5.345 | 6.1802 | 7.996 | 7.74 | 5.89 | 5.58 | 5.66 | 6.89 | 8.09 | 7.53 | 6.8031 | 6.95 | 6.0646 | 6.28 | #N/A | 6.78 | 7.21 | 5.72
O2 emissions - 30% |  |  | 30 | 7.57 | #N/A | #N/A | 6.5931 | #N/A | 8.16 | 6.27 | 5.97 | 6.08 | 7.28 | 8.61 | 8.04 | 7.2482 | 7.36 | #N/A | 6.679 | #N/A | #N/A | 7.43 | 6.12
O2 emissions - 40% |  |  | 40 | 8.07 | 8.62 | 6.5875 | 7.2627 | 9.4099 | 8.63 | 6.84 | 6.65 | 6.69 | 7.91 | 9.24 | 8.82 | 7.8411 | 7.95 | 7.2495 | 7.415 | #N/A | 7.64 | 7.68 | 6.69
O2 emissions - 50% |  |  | 50 | #N/A | 9.87 | #N/A | 7.9652 | #N/A | 9.01 | #N/A | 7.34 | 7.3 | 8.59 | 9.81 | 9.67 | #N/A | 8.58 | #N/A | 7.884 | #N/A | #N/A | 7.81 | 7.29
O2 emissions - 60% |  |  | 60 | #N/A | 10.54 | #N/A | 8.3798 | #N/A | 9.26 | #N/A | 8.05 | 7.86 | 9.23 | 10.5 | 10.4 | #N/A | 9.26 | #N/A | 8.8408 | #N/A | #N/A | 7.91 | 7.89
|  | Unburnt UHC emissions | ppm
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 249.7109 | 480.9623 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4230.1986 | #N/A | 1728.1128 | #N/A | 712.7904 | #N/A | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | 94.9357 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1543.5404 | #N/A | 505.5917 | #N/A | 232.3066 | #N/A | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 34.6727 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | 94.05 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | 91.04 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda)
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 1.3953 | 1.3953 | 1.2459 | 1.2941 | 1.3987 | 1.3944 | 1.2805 | 1.2448 | 1.2567 | 1.4028 | 1.3619 | 1.378 | 1.351 | 1.4009 | 1.2947 | 1.2869 | #N/A | 1.3743 | 1.4028 | 1.2628
Air Excess (Lambda) - 10% |  |  | 10 | 1.4706 | #N/A | #N/A | 1.3442 | #N/A | 1.4758 | 1.3241 | 1.2923 | 1.3019 | 1.4257 | 1.4831 | 1.4483 | 1.4049 | 1.4325 | #N/A | 1.3359 | #N/A | #N/A | 1.4624 | 1.3109
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | 1.3987 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4608 | #N/A | #N/A | 1.4042 | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | 1.5262 | 1.5054 | 1.3414 | 1.417 | 1.6149 | 1.5837 | 1.3898 | 1.3619 | 1.369 | 1.4883 | 1.6266 | 1.559 | 1.4792 | 1.4947 | 1.4061 | 1.4266 | #N/A | 1.4768 | 1.5228 | 1.3743
Air Excess (Lambda) - 30% |  |  | 30 | 1.5637 | #N/A | #N/A | 1.4576 | #N/A | 1.6355 | 1.4257 | 1.3972 | 1.4075 | 1.5306 | 1.6949 | 1.6204 | 1.5271 | 1.5396 | #N/A | 1.4664 | #N/A | #N/A | 1.5475 | 1.4113
Air Excess (Lambda) - 40% |  |  | 40 | 1.6241 | 1.6963 | 1.4571 | 1.5287 | 1.8119 | 1.6977 | 1.4831 | 1.4634 | 1.4675 | 1.6043 | 1.7857 | 1.7241 | 1.5959 | 1.6092 | 1.5272 | 1.5458 | #N/A | 1.5719 | 1.5766 | 1.4675
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | 1.8868 | #N/A | 1.6111 | #N/A | 1.7515 | #N/A | 1.5373 | 1.5328 | 1.6922 | 1.8767 | 1.8535 | #N/A | 1.6908 | #N/A | 1.6011 | #N/A | #N/A | 1.5921 | 1.5317
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | 2.0076 | #N/A | 1.664 | #N/A | 1.7888 | #N/A | 1.6216 | 1.5982 | 1.7842 | 2 | 1.9811 | #N/A | 1.7888 | #N/A | 1.7271 | #N/A | #N/A | 1.6043 | 1.6018
Qmin
|  | H2 | %
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | 10.1 | #N/A | #N/A | 10.0154 | #N/A | 10.2 | 10 | 10.4 | 10.2 | 10.1 | 10 | 10 | 10 | 10.8 | #N/A | #N/A | 40 | #N/A | 9.9 | 10.1
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | 19.5172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20 | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A
H2 - 23% |  |  | 23 | 23.2 | 23.5 | 22.2 | 22.4735 | 23.3178 | 23.2 | 23 | 23.4 | 23.6 | 22.7 | 23 | 23 | 23 | 23.2 | 23.82 | 23 | 23 | 23.7498 | 23.2 | 23.1
H2 - 30% |  |  | 30 | 30.2 | #N/A | #N/A | 29.392 | #N/A | 30.2 | 30 | 30.5 | 30.7 | 30 | 30 | 30 | 30 | 30.3 | #N/A | #N/A | 40 | #N/A | 29.8 | 29.8
H2 - 40% |  |  | 40 | 40.3 | 39.7 | 37.9 | 37.7308 | 40.2807 | 40.1 | 40.1 | 40.4 | 40.6 | 40.2 | 40 | 40 | 40 | 40 | 41.12 | 40.16 | 40 | 41.0782 | 39.8 | 40.2
H2 - 50% |  |  | 50 | #N/A | 49.8 | #N/A | 47.8278 | #N/A | 49.9 | #N/A | 50.1 | 49.6 | 49.5 | #N/A | #N/A | #N/A | 50 | #N/A | #N/A | 40 | #N/A | 49.6 | 50.3
H2 - 60% |  |  | 60 | #N/A | 59.2 | #N/A | 59.3377 | #N/A | 60 | #N/A | 59.8 | #N/A | 59.4 | #N/A | #N/A | #N/A | 59.4 | #N/A | 60.16 | 40 | #N/A | #N/A | 60.1
|  | Wobbe index | [MJ/m³]
Wobbe index - 0% |  | %H2 in test gas | 0 | 53.4706 | 50.6063 | 50.6063 | 50.5385 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6038 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063
Wobbe index - 10% |  |  | 10 | 52.1605 | #N/A | #N/A | 49.3086 | #N/A | 49.354 | 49.354 | 49.3294 | 49.354 | 49.3664 | 49.3417 | 49.354 | 49.3787 | 49.2802 | #N/A | #N/A | 45.7145 | #N/A | 49.391 | 49.3664
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | 48.1364 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 48.1467 | #N/A | #N/A | #N/A | 45.7145 | #N/A | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | 50.4558 | 47.7161 | 47.8759 | 47.7716 | 47.7376 | 47.753 | 47.7899 | 47.7284 | 47.7038 | 47.8145 | 47.8022 | 47.8391 | 47.7776 | 47.753 | 47.6768 | 47.7776 | 47.7776 | 47.6854 | 47.753 | 47.7653
Wobbe index - 30% |  |  | 30 | 49.5499 | #N/A | #N/A | 46.9218 | #N/A | 46.8956 | 46.8956 | 46.859 | 46.8347 | 46.92 | 46.9566 | 46.8956 | 46.92 | 46.8834 | #N/A | #N/A | 45.7145 | #N/A | 46.9444 | 46.9444
Wobbe index - 40% |  |  | 40 | 48.2643 | 45.7501 | 45.9647 | 45.9119 | 45.6808 | 45.7026 | 45.7026 | 45.667 | 45.6433 | 45.6907 | 45.7145 | 45.7263 | 45.7145 | 45.7145 | 45.5818 | 45.6955 | 45.7145 | 45.5868 | 45.7382 | 45.6907
Wobbe index - 50% |  |  | 50 | #N/A | 44.5802 | #N/A | 44.727 | #N/A | 44.569 | #N/A | 44.5466 | 44.6026 | 44.6138 | #N/A | #N/A | #N/A | 44.5578 | #N/A | #N/A | 45.7145 | #N/A | 44.6026 | 44.5243
Wobbe index - 60% |  |  | 60 | #N/A | 43.5791 | #N/A | 43.5674 | #N/A | #N/A | #N/A | 43.5196 | #N/A | 43.5592 | #N/A | #N/A | #N/A | 43.5592 | #N/A | 43.4842 | 45.7145 | #N/A | #N/A | 43.4901
|  | Efficiency (Hi) | % on Hi
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 102.7407 | 102.7 | 105.599 | 100.8778 | 97.4525 | 103.5689 | 101.8621 | 100.8972 | 101.6 | 101.5 | 101.8 | 99.2 | #N/A | 95.1 | 103.8487 | 101.1842 | 101.1206 | 103.213 | 103.9 | 101.3
Efficiency (Hi) - 10% |  |  | 10 | 104.1914 | #N/A | #N/A | 99.9539 | #N/A | 102.5977 | 101.3741 | 104.5149 | 101.3 | 102.1 | 101.8 | 99.9 | #N/A | 95.8 | #N/A | #N/A | #N/A | #N/A | 104.1 | 101.1
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | 99.9285 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | 103.663 | 104 | 103.8786 | 99.3193 | 98.3833 | 104.0906 | 100.5831 | 103.912 | 101.9 | 102.9 | 102.6 | 100.2 | #N/A | 96.3 | 103.897 | 107.0921 | 103.5452 | 101.7255 | 104.7 | 101.6
Efficiency (Hi) - 30% |  |  | 30 | 105.4832 | #N/A | #N/A | 99.6869 | #N/A | 104.8038 | 101.2237 | 105.261 | 102.2 | 103.3 | 103 | 101.4 | #N/A | 96.3 | #N/A | #N/A | #N/A | #N/A | 104.8 | 101.9
Efficiency (Hi) - 40% |  |  | 40 | 106.2303 | 106.8 | 104.6837 | 99.5726 | 99.4567 | 105.2366 | 102.6921 | 104.1541 | 102.8 | 104.1 | 103.8 | 101.8 | #N/A | 96.7 | 103.218 | 104.7843 | 104.2151 | 100.9886 | 105.8 | 102.5
Efficiency (Hi) - 50% |  |  | 50 | #N/A | 103.4 | #N/A | 99.1496 | #N/A | 105.9241 | #N/A | 103.2901 | 103.7 | 104.9 | #N/A | #N/A | #N/A | 97.7 | #N/A | #N/A | #N/A | #N/A | 106.7 | 103.4
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 105.2 | #N/A | 106.5 | #N/A | #N/A | #N/A | #N/A | #N/A | 98.4002 | #N/A | #N/A | #N/A | 104.2
|  | CO emissions | ppm
CO emissions - 0% |  | %H2 in test gas | 0 | 20.3238 | 14.1062 | 18.1647 | 0.76676 | 1.2672 | 9.9 | 19.3 | 5.9 | 52.7 | 7.4 | 5.3 | 7.3 | 15.0387 | 11.5 | 5.4041 | 22.0245 | 12.9877 | 12.4266 | 12.72 | 22.5
CO emissions - 10% |  |  | 10 | 19.0354 | #N/A | #N/A | 0.78802 | #N/A | 8.7 | 17.3 | 5.4 | 53.5 | 6.7 | 5 | 6.9 | 14.8236 | 12 | #N/A | #N/A | #N/A | #N/A | 10.57 | 21.1
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 0.20916 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 13.9938 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | 18.0094 | 2.9342 | 14.4561 | 1.2291 | 1.1754 | 7.8 | 16.7 | 4.7 | 48.2 | 5.8 | 4.8 | 6.3 | 14.2628 | 11.1 | 5.4331 | 14.9618 | 6.2721 | 15.6525 | 9.24 | 19.8
CO emissions - 30% |  |  | 30 | 17.4486 | #N/A | #N/A | 0.71717 | #N/A | 7.4 | 16.9 | 4.2 | 51.2 | 5.1 | 4.7 | 5.9 | 14.5528 | 9.2 | #N/A | #N/A | #N/A | #N/A | 8.5 | 19.2
CO emissions - 40% |  |  | 40 | 15.8608 | 3.3825 | 12.8435 | 0.34545 | 0.62694 | 7 | 17.5 | 3.6 | 51.2 | 4.8 | 4.6 | 5.3 | 15.3233 | 7.1 | 6.8533 | 22.0557 | 2.6437 | 10.6658 | 7.69 | 18.5
CO emissions - 50% |  |  | 50 | #N/A | 2.9756 | #N/A | 0.17826 | #N/A | 6.3 | #N/A | 3 | 50.9 | 4.4 | #N/A | #N/A | #N/A | 5.8 | #N/A | #N/A | #N/A | #N/A | 7.14 | 18.2
CO emissions - 60% |  |  | 60 | #N/A | 1.5807 | #N/A | 1.2727 | #N/A | #N/A | #N/A | 2.4 | #N/A | 3.8 | #N/A | #N/A | #N/A | 4.8 | #N/A | 23.8546 | #N/A | #N/A | #N/A | 17.1
|  | NOx emissions | ppm
NOx emissions - 0% |  | %H2 in test gas | 0 | 9.7379 | 20.4541 | 25.6518 | 10.9511 | 8.5545 | 11.9 | 21.4 | 14.1 | 8.5 | 7.1 | 16 | 31.5 | 17.5909 | 16.9 | 15.3696 | 12.0999 | 32.5004 | 3.6162 | 19.63 | 23.7
NOx emissions - 10% |  |  | 10 | 9.1881 | #N/A | #N/A | 7.897 | #N/A | 10.7 | 15.5 | 10.9 | 6.9 | 6.7 | 16.4 | 31.9 | 14.6993 | 15.5 | #N/A | #N/A | #N/A | #N/A | 16.44 | 17.1
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 6.3516 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.051 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | 8.2695 | 16.1381 | 21.3549 | 6.1018 | 7.5545 | 9.9 | 11.3 | 8.7 | 5.7 | 6.2 | 16.6 | 30.3 | 11.6118 | 13.8 | 9.1878 | 9.0149 | 18.6433 | 2.3355 | 14.19 | 12.7
NOx emissions - 30% |  |  | 30 | 7.9037 | #N/A | #N/A | 5.0205 | #N/A | 9.5 | 9.3 | 7.3 | 4.9 | 5.9 | 16.6 | 29.3 | 9.5192 | 13 | #N/A | #N/A | #N/A | #N/A | 13.2 | 10.5
NOx emissions - 40% |  |  | 40 | 7.1772 | 15.7288 | 19.0984 | 4.1081 | 6.8753 | 8.7 | 7.2 | 6 | 3.9 | 5.4 | 16.1 | 26 | 8.4419 | 11.9 | 6.5069 | 5.5965 | 11.3707 | 2.6104 | 12.4 | 7.9
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | 3.3341 | #N/A | 7.9 | #N/A | 4.9 | 3 | 5.1 | #N/A | #N/A | #N/A | 10.5 | #N/A | #N/A | #N/A | #N/A | 11.94 | 5.8
NOx emissions - 60% |  |  | 60 | #N/A | 7.2713 | #N/A | 2.6752 | #N/A | #N/A | #N/A | 4 | #N/A | 4.7 | #N/A | #N/A | #N/A | 9.7 | #N/A | 3.0409 | #N/A | #N/A | #N/A | 5.3
|  | Qtest (input) | kW
Qtest (input) - 0% |  | %H2 in test gas | 0 | 7.7621 | 4.4328 | 3.8089 | 4.35 | 2.5608 | 6.5077 | 5.2816 | 5.8475 | 3.8669 | 2.6408 | 2.9238 | 5.093 | 4.7417 | 4.9044 | 2.0266 | 9.0704 | 6.9825 | 2.6777 | 6.4134 | 4.9987
Qtest (input) - 10% |  |  | 10 | 7.5822 | #N/A | #N/A | 4.2457 | #N/A | 6.4816 | 5.0802 | 5.5973 | 3.7663 | 2.542 | 2.8883 | 5.0802 | 4.7573 | 4.8829 | #N/A | #N/A | #N/A | #N/A | 6.3646 | 4.9788
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | 4.0976 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.6518 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | 7.7279 | 4.2169 | 3.8139 | 4.0766 | 2.503 | 6.3214 | 4.9114 | 5.6009 | 3.6227 | 2.5391 | 2.7748 | 5.0867 | 4.5992 | 4.8991 | 1.9931 | 8.1553 | 6.4673 | 2.4695 | 6.3056 | 4.9111
Qtest (input) - 30% |  |  | 30 | 7.5369 | #N/A | #N/A | 3.9668 | #N/A | 6.2498 | 4.7617 | 5.4911 | 3.4814 | 2.5342 | 2.7651 | 5.0593 | 4.5083 | 4.6832 | #N/A | #N/A | #N/A | #N/A | 6.2869 | 4.9205
Qtest (input) - 40% |  |  | 40 | 7.5059 | 4.0133 | 3.7554 | 3.8536 | 2.464 | 6.1766 | 4.5476 | 5.5495 | 3.3772 | 2.5089 | 2.7176 | 5.0325 | 4.3433 | 4.6879 | 1.898 | 7.9826 | 6.1817 | 2.3455 | 6.2286 | 4.8958
Qtest (input) - 50% |  |  | 50 | #N/A | 4.0084 | #N/A | 3.7298 | #N/A | 6.0798 | #N/A | 5.5765 | 3.2653 | 2.467 | #N/A | #N/A | #N/A | 4.601 | #N/A | #N/A | #N/A | #N/A | 6.1857 | 4.8369
Qtest (input) - 60% |  |  | 60 | #N/A | 4.0133 | #N/A | 3.6012 | #N/A | #N/A | #N/A | 5.5982 | #N/A | 2.4265 | #N/A | #N/A | #N/A | 4.5773 | #N/A | 7.9494 | #N/A | #N/A | #N/A | 4.8124
|  | Flue gases temperatures | [°C]
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 42 | #N/A | 56.8995 | 65.9768 | 50.3315 | 46.09 | 49.6 | 44.2 | 39.5 | 48.3 | 42.8 | 52 | 53.19 | 56.4 | 76.571 | 40.4412 | 48.01 | 53.35 | 44.3 | 49.6
Flue gases temperatures - 10% |  |  | 10 | 42.75 | #N/A | #N/A | 65.1678 | #N/A | 46.09 | 49.5 | 44.2 | 39.7 | 48.1 | 42.8 | 52.1 | 51.5727 | 56.6 | #N/A | #N/A | #N/A | #N/A | 44.5 | 49.6
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | 64.638 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 51.7178 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | 42.34 | #N/A | 56.9485 | 64.4132 | 50.4635 | 46.11 | 49.1 | 44.3 | 39.7 | 47.9 | 42.8 | 52.1 | 51.6548 | 56.6 | 75.1544 | 40.04 | 46.97 | 52.32 | 44.5 | 49.7
Flue gases temperatures - 30% |  |  | 30 | 42.58 | #N/A | #N/A | 63.9275 | #N/A | 46.14 | 48.9 | 44.3 | 39.8 | 47.9 | 42.8 | 52.1 | 51.7355 | 56.9 | #N/A | #N/A | #N/A | #N/A | 44.4 | 49.8
Flue gases temperatures - 40% |  |  | 40 | 42.69 | #N/A | 57.0122 | 63.0569 | 50.5759 | 46.11 | 48.8 | 44.4 | 39.8 | 47.9 | 42.7 | 52.1 | 53.1351 | 57 | 73.7975 | 40.9047 | 45.13 | 51.86 | 44.4 | 49.8
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | 62.2686 | #N/A | 46.05 | #N/A | 44.5 | 39.7 | 47.9 | #N/A | #N/A | #N/A | 57.2 | #N/A | #N/A | #N/A | #N/A | 44.2 | 49.9
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | 62.9314 | #N/A | #N/A | #N/A | 44.6 | #N/A | 47.8 | #N/A | #N/A | #N/A | 57.3 | #N/A | 40.7693 | #N/A | #N/A | #N/A | 50.2
|  | CO2 emissions | [%]
CO2 emissions - 0% |  | %H2 in test gas | 0 | 8.2884 | 8.25 | 9.3156 | 8.1068 | 7.8551 | 8.33 | 8.84 | 9.06 | 7.74 | 7.62 | 8.95 | 9.54 | 8.4129 | 8.59 | 8.6624 | 8.56 | 9.31 | 7.08 | 9.13 | 9.33
CO2 emissions - 10% |  |  | 10 | 8.089 | #N/A | #N/A | 7.5951 | #N/A | 8.04 | 8.17 | 8.46 | 7.18 | 7.39 | 8.86 | 9.37 | 7.9504 | 8.2 | #N/A | #N/A | #N/A | #N/A | 8.92 | 8.63
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 7.0667 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.5722 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | 7.7837 | 7.43 | 8.5619 | 6.9062 | 7.3587 | 7.65 | 7.49 | 7.72 | 6.57 | 7.06 | 8.75 | 8.96 | 7.3087 | 7.71 | 7.7106 | 7.51 | 8.2 | 6.0154 | 8.54 | 7.87
CO2 emissions - 30% |  |  | 30 | 7.6408 | #N/A | #N/A | 6.5359 | #N/A | 7.42 | 7.07 | 7.39 | 6.15 | 6.85 | 8.68 | 8.71 | 6.8964 | 7.42 | #N/A | #N/A | #N/A | #N/A | 8.3 | 7.44
CO2 emissions - 40% |  |  | 40 | 7.3069 | 6.01 | 7.9886 | 6.0826 | 6.8782 | 7.02 | 6.47 | 6.69 | 5.61 | 6.51 | 8.57 | 8.36 | 6.2557 | 6.94 | 6.7779 | 6.45 | 7.14 | 6.3 | 7.97 | 6.79
CO2 emissions - 50% |  |  | 50 | #N/A | 6.42 | #N/A | 5.4599 | #N/A | 6.53 | #N/A | 5.95 | 5.09 | 6.1 | #N/A | #N/A | #N/A | 6.4 | #N/A | #N/A | #N/A | #N/A | 7.6 | 6.1
CO2 emissions - 60% |  |  | 60 | #N/A | 5.58 | #N/A | 4.9948 | #N/A | #N/A | #N/A | 5.17 | #N/A | 5.56 | #N/A | #N/A | #N/A | 5.81 | #N/A | 5.17 | #N/A | #N/A | #N/A | 5.35
|  | O2 emissions | [%]
O2 emissions - 0% |  | %H2 in test gas | 0 | 5.8563 | 5.7 | 4.2847 | 6.4205 | 6.8912 | 5.88 | 5.01 | 4.64 | 6.8 | 7.04 | 5.06 | 3.82 | 5.8034 | 5.26 | 5.1183 | 5.98 | #N/A | 8.29 | 4.57 | 4.1
O2 emissions - 10% |  |  | 10 | 5.8417 | #N/A | #N/A | 7.0502 | #N/A | 6.01 | 5.75 | 5.29 | 7.42 | 7.11 | 4.82 | 3.88 | 6.2651 | 5.54 | #N/A | #N/A | #N/A | #N/A | 4.6 | 4.84
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 7.673 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6.6457 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | 5.7841 | 6.11 | 4.4932 | 7.8621 | 6.93 | 6.13 | 6.4 | 6.08 | 7.99 | 7.21 | 4.42 | 3.8 | 6.8897 | 5.86 | 6.3335 | 6.63 | #N/A | 9.633 | 4.61 | 5.55
O2 emissions - 30% |  |  | 30 | 5.7033 | #N/A | #N/A | 8.2865 | #N/A | 6.19 | 6.79 | 6.3 | 8.43 | 7.25 | 4.14 | 4.06 | 7.3255 | 6.02 | #N/A | #N/A | #N/A | #N/A | 4.6 | 5.93
O2 emissions - 40% |  |  | 40 | 5.6614 | 6.1 | 4.5613 | 8.7905 | 6.9912 | 6.29 | 7.32 | 6.99 | 8.92 | 7.25 | 3.56 | 4.03 | 7.9943 | 6.3 | 7.181 | 7.81 | #N/A | 8.35 | 4.47 | 6.51
O2 emissions - 50% |  |  | 50 | #N/A | 6.18 | #N/A | 9.3622 | #N/A | 6.41 | #N/A | 7.68 | 9.39 | 7.32 | #N/A | #N/A | #N/A | 6.56 | #N/A | #N/A | #N/A | #N/A | 4.61 | 7.08
O2 emissions - 60% |  |  | 60 | #N/A | 6.45 | #N/A | 9.242 | #N/A | #N/A | #N/A | 8.37 | #N/A | 7.5 | #N/A | #N/A | #N/A | 6.74 | #N/A | 9.12 | #N/A | #N/A | #N/A | 7.62
|  | Unburnt UHC emissions | ppm
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1023.6336 | #N/A | #N/A | #N/A | #N/A | 786.2493 | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 443.6043 | #N/A | 218.8244 | #N/A | #N/A | 273.2976 | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda)
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 1.3867 | 1.3725 | 1.2563 | 1.4404 | 1.4884 | 1.3889 | 1.3133 | 1.2836 | 1.4789 | 1.5043 | 1.3174 | 1.2224 | 1.3819 | 1.3342 | 1.3223 | 1.3981 | #N/A | 1.6522 | 1.2781 | 1.2426
Air Excess (Lambda) - 10% |  |  | 10 | 1.3854 | #N/A | #N/A | 1.5054 | #N/A | 1.4009 | 1.377 | 1.3367 | 1.5464 | 1.5119 | 1.2979 | 1.2266 | 1.4252 | 1.3583 | #N/A | #N/A | #N/A | #N/A | 1.2805 | 1.2995
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | 1.5757 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.463 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | 1.3801 | 1.4103 | 1.2722 | 1.5984 | 1.4925 | 1.4122 | 1.4384 | 1.4075 | 1.6141 | 1.5228 | 1.2666 | 1.2209 | 1.4883 | 1.3871 | 1.4318 | 1.4614 | #N/A | 1.8475 | 1.2813 | 1.3592
Air Excess (Lambda) - 30% |  |  | 30 | 1.3728 | #N/A | #N/A | 1.6518 | #N/A | 1.418 | 1.4778 | 1.4286 | 1.6706 | 1.5273 | 1.2456 | 1.2397 | 1.5357 | 1.4019 | #N/A | #N/A | #N/A | #N/A | 1.2805 | 1.3935
Air Excess (Lambda) - 40% |  |  | 40 | 1.3691 | 1.4094 | 1.2775 | 1.72 | 1.4991 | 1.4276 | 1.5351 | 1.4989 | 1.7384 | 1.5273 | 1.2041 | 1.2375 | 1.6147 | 1.4286 | 1.5197 | 1.5921 | #N/A | 1.6601 | 1.2704 | 1.4493
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | 1.417 | #N/A | 1.8045 | #N/A | 1.4393 | #N/A | 1.5766 | 1.8088 | 1.5351 | #N/A | #N/A | #N/A | 1.4543 | #N/A | #N/A | #N/A | #N/A | 1.2813 | 1.5086
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | 1.4433 | #N/A | 1.786 | #N/A | #N/A | #N/A | 1.6627 | #N/A | 1.5556 | #N/A | #N/A | #N/A | 1.4727 | #N/A | 1.7677 | #N/A | #N/A | #N/A | 1.5695
Efficiency, CO & NOx at Qmax
Efficiency Qmax
|  | Eff Q max | a | 0.05 | -0.053 | 0.0496 | -0.0145 | 0.011 | na | 0.0367 | 0.0417 | 0.0496 | 0.04 | 0.025 | 0.026 | 0.045
|  |  | b | 94.12 | 103.29 | 101.82 | 101.89 | 107.65 | na | 100.46 | 99.57 | 101.82 | 99.57 | 98.49 | 102.87 | 94.36
|  |  | r2 | 0.6 | 0.88 | 0.9546 | 0.57 | 0.91 | na | 0.9 | 0.93 | 0.95 | 0.98 | 0.74 | 0.82 | 0.4284
|  | CO Q max | a | -0.42 | -1.21 | -4 | -1.17 | -1.26 | -0.63 | -0.81 | -0.4 | -0.57 | -1.26 | 0.63 | 2.62 | -2.46
|  |  | b | 44.4 | 65.9 | 210 | 71.76 | 55.6 | 73.5 | 59 | 30 | 66.7 | 90.7 | 18.4 | 56.8 | 12
|  |  | r2 | 0.97 | 0.88 | 0.99 | 0.92 | 0.91 | 0.91 | 0.985 | 0.93 | 0.91 | 0.98 | 0.7 | 0.75 | 0.96
|  | NOx Q max | a | -0.36 | -0.13 | -0.57 | -0.33 | -0.35 | -0.19 | -0.63 | -0.85 | -0.53 | -0.19 | -0.25 | -0.26 | -0.145
|  |  | b | 24.61 | 11.2 | 37.2 | 24.5 | 17 | 14.8 | 40.4 | 54.31 | 40.4 | 20.11 | 16 | 18.4 | 10.9
|  |  | r2 | 0.96 | 0.92 | 0.99 | 0.92 | 0.96 | 0.83 | 0.98 | 0.95 | 0.93 | 0.98 | 0.8 | 0.93 | 0.97
Efficiency, CO & NOx at Qmin
|  | Efficiency Qmin | [15 empty] | GW13 | GW14
|  |  | a | 0.0756 | 0.0394 | -0.0245 | -0.028 | 0.0394 | na | 0.0365 | 0.01 | 0.0437 | 0.0786 | 0.0516 | 0.1215 | 0.29 |  | 1.023 | 2.023
|  |  | b | 97.467 | 103.11 | 99.77 | 100.48 | 103.11 | na | 100.53 | 107.28 | 101.14 | 101.22 | 101.54 | 95.58 | 106.16 |  | 97.5 | 98.5
|  |  | r2 | 0.82 | 0.23 | 0.36 | 0.72 | 0.98 | na | 0.79 | 0.008 | 0.85 | 0.96 | 0.93 | 0.79 | 0.6937 |  | 1.8559 | 2.8559
CO Qmin
|  |  | a | -0.15 | -0.18 | 0.13 | 0.02 | -0.015 | -0.087 | 0.33 | -0.06 | 0.32 | -0.086 | -0.035 | -0.06 | -0.092 |  | 0.26 | 1.26
|  |  | b | 28.54 | 11.44 | 18 | 0.68 | 1.34 | 13.4 | 21.25 | 7.79 | 78.6 | 11 | 6.83 | 8.9 | 9 |  | 95.2 | 96.2
|  |  | r2 | 0.98 | 0.74 | 0.98 | 5e-06 | 0.79 | 0.97 | 0.84 | 0.99 | 0.79 | 0.98 | 0.99 | 0.99 | 0.98 |  | 1.89 | 2.89
NOx Qmin
|  |  | a | -0.09 | -0.2 | -0.16 | -0.13 | -0.04 | -0.097 | -0.26 | -0.18 | -0.14 | -0.056 | -0.04 | -0.16 | -0.26 |  | 2.17 | 3.17
|  |  | b | 13.75 | 21.15 | 25.5 | 9.53 | 8.54 | 16.4 | 24.7 | 16.9 | 12.6 | 10.8 | 21.22 | 39.63 | 19.5 |  | 250 | 251
|  |  | r2 | 0.99 | 0.88 | 0.99 | 0.92 | 0.99 | 0.99 | 0.94 | 0.96 | 0.99 | 0.99 | 0.66 | 0.8 | 0.96 |  | 1.96 | 2.96
[18 empty] | 1.016 | 2.016
[18 empty] | 94.9 | 95.9
[18 empty] | 1.74 | 2.74
[18 empty] | 4.56 | 5.56
[18 empty] | 257.7 | 258.7
[18 empty] | 1.47 | 2.47
[18 empty] | 1.57 | 2.57
[18 empty] | 390 | 391
[18 empty] | 1.86 | 2.86
mauvais copiercoller?

## Seg100b Non Premix Boiler
Do not touch this colum | THyGA Segment 100b - Non Premix Boiler |  |  | THyGA Test data - Values | [10 empty] | Graph for the indicator (KPI): |  |  |  |  | Efficiency (Hi)
|  |  |  | GA01 | GA16v01 | EB02v04 | GW02V04 | GW03V04 | GW04V04 | GW12V03 | EN03V01 | GW16V01 | BA01 | GW18 |  | GA01 | GA16v01 | EB02v04 | GW02V04 | GW03V04 | GW04V04 | GW12V03 | EN03V01 | GW16V01 | BA01 | GW18
| SEGMENT Nr |  |  | GA1_SEGM_101 | GA16_SEGM_102 | EB02_SEGM_102 | GW2_SEGM_102 | GW03_SEGM_103 | GW04_SEGM_105 | GWI12_SEGM_107 | EN03_SEGM_101 | GWI_16_SEGM_107 | See QA in the test sheet. Add question on details for flue pipe lengh | GW18_SEGM_109
|  | Report test lab code |  | 101 | 102 | 102 | 102 | 103 | 105 | 107 | 101 | 107 | 107 | 109 | Qmax | Graph title | THyGA Segment 100b - Non Premix Boiler - Efficiency (Hi) at Qmax | [5 empty] | Y axis | Efficiency (% in Hi)
|  | Appliance type code (B, CH, CO, F, WH,O) (*) |  | GA1 | GA16 | EB02 | GW2 | GW03 | GW04 | GWI12 | EN03 | GWI_16 | BA01 | GW18 | %H2 | GA01 | GA16 | EB02 | GW02 | GW03 | GW04 | GW12 | EN03 | GW16 | BA01 | GW18
|  | Appliance type |  | B | B | Open Flued Boiler (B) | B | B | B | B | CH | B | B | B | 0 | 81.1037 | 84.7905 | 86.2717 | 89.9421 | 89.9 | 92.1 | 96.7 | 93.1782 | 99.3 | 98.05 | 95.5
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 10 | #N/A | #N/A | #N/A | 89.7973 | 89.6 | 92.4 | 96.8 | #N/A | 99.8 | 97.8 | 96.6
|  | Burner type |  | Atmospheric | Atmosperhic | Natural gas brenner | atmo | atmospheric | Atmospheric burner | partial pre mixed burner | atmospherique | Condensing Boiler | premix low nox tech burner | Forced draught | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 98.15 | #N/A
|  | For cooker hobs: burner tested? |  | NA | n | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 0 | 23 | #N/A | 85.7476 | 86.3883 | 90.3181 | 89.8 | 92.5 | 96.8 | 98.9023 | 99.6 | 97.75 | 97
|  | Modulating burner (Y/N) |  | Y | n | Y | Y | N | Y | Y | N | Y | Y | Y | 30 | 81.4242 | #N/A | 87.2238 | 90.4605 | 90.1 | 92.6 | 96.9 | #N/A | 99.4 | 97.88 | 97
|  | Pressure regulator (Y/N) |  | Y | n | Y | Y | Y | Y | Y | 0 | Y | Y | Y | 40 | #N/A | 84.8437 | 86.8972 | 90.7387 | 90.6 | 92.1 | 97.5 | 99.9858 | 100.2 | 97.8 | 96.7
|  | Can the appliance be adjusted (Y/N) |  | N | n | N | Y | Y | N | N | N | N | Y | N | 50 | 81.2388 | #N/A | #N/A | 90.9132 | 90.6 | 92.4 | 97.9 | #N/A | 100.1 | 97.85 | 98.1
|  | Is the appliance equiped with a combustion control (Y/N) |  | 0 | n | Y | N | N | N | N | N | N | Y | Y | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 92.7 | 97.9 | #N/A | 100.4 | 97.9 | 98.2
|  | If the appliance can be adjusted. Instructions: |  | N | n | 0 | 0 | The CO2 levels and the power output of the system were kept constant as by G20, as given by the manufacturer instruction manual | 0 | 0 | N | 0 |  | This burner system is a so-called forced draught burner, i.e. the combustion air is supplied by the burner's own blower. This system also has an integrated combustion management system that includes electronic ignition, flame monitoring by ionization electrode and load control, as well as the necessary safety functionality. With this type of burner, the ability to influence the operating parameters is limited by design. It is only possible to vary the output at predefined intervals and to make a rough setting for the combustion air ratio. The burner is controlled manually by means of operating keys and a display.
|  | If Yes what technology is used? |  | NA | n | Atmospheric | 0 | 0 | 0 | 0 | 0 | 0 | PGS | 0
|  | Max. power input (net) [kW] |  | 25.8 | 27.5 | 26.5 | 22.2 | 17 | 22.2 | 25 | 34.87 | 22.6 | 24.8 | 100 | Qmin | Graph title | THyGA Segment 100b - Non Premix Boiler - Efficiency (Hi) at Qmin | [5 empty] | Y axis | Efficiency (% in Hi)
|  | Min. power input (net) [kW] |  | 11 | na | 12 | 8.9 | 0 | 12 | 15 | 0 | 9.1 | 10.6 | 30 | %H2 | GA01 | GA16 | EB02 | GW02 | GW03 | GW04 | GW12 | EN03 | GW16 | BA01 | GW18
|  | Flue type |  | B11Bs | B11Bs | B | 0 | 100 | 0 | 0 | B | 0 | C12 | 0 | 0 | 81.15 | #N/A | 91.4783 | 89.8394 | #N/A | 92.2 | 94.2 | #N/A | 95.33 | 97.92 | 95.1
|  | Flue lenght |  | 1m | 1m | 0,8m | 0 | 1m | 1m | 1 m | 1M | 1 m | 1m | 0 | 10 | #N/A | #N/A | #N/A | 89.6763 | #N/A | 92 | 94 | #N/A | 96 | 98.13 | 96
|  | Applicable standard(s) |  | EN 15502 ( EN 297) | EN297 | EN 15502 | 0 | EN 15502 | 0 | 0 | 0 | 0 | EN15502-2-1 | 0 | 20 | 81.1456 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 97.87 | #N/A
|  | Gas category |  | I2E+ | I2E+ | II2ELL3P, II2H3P, II2E3P | I2ELL | E/H natural gas | II2ELL3P | II2H3P | II2E+3+ | II2H3P | II2H3P | 0 | 23 | #N/A | #N/A | 92.2326 | 89.9301 | #N/A | 91.9 | 94 | #N/A | 95.95 | 97.52 | 96.7
|  | Origin of the appliance |  | Already used for other project . Received september 2016 . | Already used for other project | Old/Used by DVGW-EBI | own by GWI, old tested before | old/used by GWI | old/used by GWI | New | Customer | New | BAXI S.p.A. | old/used in another lab at GWI | 30 | 81.4845 | #N/A | #N/A | 90.2457 | #N/A | 91.9 | 94.2 | #N/A | 95.63 | 97.91 | 97.7
|  | Manufacture year |  | 2016 | 2004 | 2019 | 2005 | 2002 | 0 | 0 | 1997 | 2021 | 2021 | 2002 | 40 | #N/A | #N/A | 92.3171 | 90.6033 | #N/A | 92 | 94.7 | #N/A | 95.79 | 97.8 | 98.3
[15 empty] | 50 | 78.5489 | #N/A | #N/A | #N/A | #N/A | 92.4 | 94.7 | #N/A | 96.13 | 97.38 | 99
[15 empty] | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 92.4 | 95 | #N/A | #N/A | 97.75 | 99.1
QMAX
H2
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | #N/A | #N/A | 10.2 | 10 | 10.6 | 10.4 | #N/A | 10.4 | 10 | 10
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20 | #N/A
H2 - 23% |  |  | 23 | #N/A | 22.9 | 23 | 23.3 | 23.2 | 23.6 | 23 | 23.07 | 23 | 23 | 23
H2 - 30% |  |  | 30 | #N/A | #N/A | 30 | 30.4 | 30.2 | 30.5 | 29.9 |  | 29.8 | 30 | 30
H2 - 40% |  |  | 40 | #N/A | 39.8 | 40 | 40.3 | 40.1 | 40 | 40.2 | 40.62 | 40.2 | 40 | 40
H2 - 50% |  |  | 50 | 50 | #N/A | #N/A | 50 | 50 | 50 | 50.2 |  | 49.9 | 50 | 50
H2 - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | 60 | 60 | 60 | #N/A | 59.7 | 60 | 60
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6604 | 50.6063 | 53.4704 | 53.4706 | 53.4706 | 53.3636 | 50.6063 | 50.6063 | 50.6063 | 53.4706 | 51.1358
Wobbe index - 10% |  |  | 10 | #N/A | #N/A | #N/A | 52.1475 | 52.1735 | 52.0954 | 49.3294 | 50.6063 | 49.3294 | 52.1735 | 49.8196
Wobbe index - 20% |  |  | 20 | 47.8168 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 50.8718 | #N/A
Wobbe index - 23% |  |  | 23 | #N/A | 47.7899 | 50.4818 | 50.4428 | 50.4558 | 50.4039 | 47.7776 | 47.769 | 47.7776 | 50.4818 | 48.104
Wobbe index - 30% |  |  | 30 | 45.7405 | #N/A | 49.5757 | 49.5241 | 49.5499 | 49.5113 | 46.9322 | 47.769 | 46.9444 | 49.5757 | 47.1685
Wobbe index - 40% |  |  | 40 | #N/A | 45.7382 | 48.3019 | 48.2643 | 48.2894 | 48.3019 | 45.6907 | 45.641 | 45.6907 | 48.3019 | 45.8554
Wobbe index - 50% |  |  | 50 | #N/A | #N/A | #N/A | 47.0503 | 47.0798 | 47.0798 | 44.5354 | 45.6813 | 44.569 | 47.0798 | 44.5833
Wobbe index - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 45.962 | 43.4999 | #N/A | 43.5295 | 45.962 | 43.3994
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 81.1037 | 84.7905 | 86.2717 | 89.9421 | 89.9 | 92.1 | 96.7 | 93.1782 | 99.3 | 98.05 | 95.5
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 89.7973 | 89.6 | 92.4 | 96.8 | #N/A | 99.8 | 97.8 | 96.6
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 98.15 | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | 85.7476 | 86.3883 | 90.3181 | 89.8 | 92.5 | 96.8 | 98.9023 | 99.6 | 97.75 | 97
Efficiency (Hi) - 30% |  |  | 30 | 81.4242 | #N/A | 87.2238 | 90.4605 | 90.1 | 92.6 | 96.9 | #N/A | 99.4 | 97.88 | 97
Efficiency (Hi) - 40% |  |  | 40 | #N/A | 84.8437 | 86.8972 | 90.7387 | 90.6 | 92.1 | 97.5 | 99.9858 | 100.2 | 97.8 | 96.7
Efficiency (Hi) - 50% |  |  | 50 | 81.2388 | #N/A | #N/A | 90.9132 | 90.6 | 92.4 | 97.9 | #N/A | 100.1 | 97.85 | 98.1
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 92.7 | 97.9 | #N/A | 100.4 | 97.9 | 98.2
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 51.1637 | 3.4472 | 86.0822 | 60.8 | 9.6 | 53 | 53.3 | 7.5749 | 107.5 | 88.7447 | 138
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 35 | 11.2 | 43.6 | 42.9 | #N/A | 75.5 | 56.0978 | 132
CO emissions - 20% |  |  | 20 | 27.1829 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 41.8128 | #N/A
CO emissions - 23% |  |  | 23 | #N/A | 2.8688 | 42.6956 | 21.4 | 14.1 | 33.3 | 34.5 | 6.9386 | 53.7 | 40.2861 | 134
CO emissions - 30% |  |  | 30 | 20.664 | #N/A | 35.8939 | 16.8 | 15.8 | 30.2 | 30.5 | #N/A | 44.8 | 29.8958 | 129
CO emissions - 40% |  |  | 40 | #N/A | 1.6088 | 26.1309 | 12.6 | 8.1 | 26.2 | 26.5 | 6.6314 | 30.6 | 22.0137 | 118
CO emissions - 50% |  |  | 50 | 14.6364 | #N/A | #N/A | 9.9 | 9.8 | 24.4 | 23.4 | #N/A | 21.9 | 16.3242 | 121
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 23.1 | 21.4 | #N/A | 14.5 | 11.9519 | 117
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | 147.62 | 67.3895 | 52.9737 | 54.4 | 25 | 29.4 | 132.8 | 103.8013 | 41.4 | 54.6587 | 34
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 41.9 | 19 | 23 | 131.6 | #N/A | 30.9 | 36.4636 | 36
NOx emissions - 20% |  |  | 20 | 122.6717 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 33.8484 | #N/A
NOx emissions - 23% |  |  | 23 | #N/A | 66.7544 | 28.9652 | 29.3 | 13.6 | 16.1 | 129.1 | 92.6925 | 21.2 | 31.1687 | 36
NOx emissions - 30% |  |  | 30 | 119.3921 | #N/A | 24.0975 | 23.1 | 13.1 | 13.1 | 127.5 | #N/A | 17.6 | 24.3438 | 37
NOx emissions - 40% |  |  | 40 | #N/A | 70.9053 | 19.3247 | 17.1 | 13.7 | 9.7 | 127.1 | 87.397 | 13.2 | 14.5291 | 39
NOx emissions - 50% |  |  | 50 | 111.3919 | #N/A | #N/A | 12.7 | 11.8 | 6.4 | 126.7 | #N/A | 9.9 | 12.593 | 39
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 4.6 | 121.6 | #N/A | 7.8 | 11.4738 | 40
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 28.3711 | 26.8171 | 28.1999 | 22.0697 | 18.9573 | 21.8875 | 26.8798 | 31.9256 | 24.1447 | 24.2349 | 100.3042
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 21.4594 | 18.4215 | 21.7441 | 26.0624 | #N/A | 23.3512 | 23.4868 | 100.6022
Qtest (input) - 20% |  |  | 20 | 26.3372 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 23.0365 | #N/A
Qtest (input) - 23% |  |  | 23 | #N/A | 24.8618 | 26.3672 | 20.5274 | 17.7 | 20.9485 | 25.0904 | 28.0169 | 22.5576 | 22.4664 | 100.5315
Qtest (input) - 30% |  |  | 30 | 25.2578 | #N/A | 25.5746 | 20.0529 | 17.3357 | 20.4804 | 24.5434 | #N/A | 22.1011 | 22.5565 | 100.5608
Qtest (input) - 40% |  |  | 40 | #N/A | 23.6605 | 24.9454 | 19.3743 | 16.8328 | 20.0424 | 23.6651 | 26.3547 | 21.2918 | 21.7668 | 100.4951
Qtest (input) - 50% |  |  | 50 | 24.8157 | #N/A | #N/A | 18.7432 | 16.2568 | 19.3241 | 22.833 | #N/A | 20.6346 | 21.4252 | 100.4012
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 18.6159 | 21.1893 | #N/A | 20.002 | 20.1647 | 100.3683
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 116.82 | 112.11 | 130.91 | 109.7 | 110.6 | 135 | 63.1 | 165.84 | 69.5 | 60.6 | 111
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | 108.7 | 109.6 | 135.3 | 63.6 | 165.89 | 69.6 | 63.2 | 110.3
Flue gases temperatures - 20% |  |  | 20 | 113.87 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 62.6 | #N/A
Flue gases temperatures - 23% |  |  | 23 | #N/A | 111.33 | 127.3201 | 106 | 108.5 | 132.9 | 63.9 | 162.32 | 69.2 | 61.7 | 109.8
Flue gases temperatures - 30% |  |  | 30 | 114.13 | #N/A | 126.2468 | 106.2 | 107.6 | 131.4 | 63.3 | 162.8 | 69 | 61.1 | 108.9
Flue gases temperatures - 40% |  |  | 40 | #N/A | 107.97 | 124.9549 | 104 | 104.6 | 130.7 | 62.2 | 160.36 | 68.7 | 59.3 | 108.7
Flue gases temperatures - 50% |  |  | 50 | 108.3439 | #N/A | #N/A | 102.3 | 101.3 | 128.7 | 62.1 | 160.07 | 67.9 | 61.4 | 108
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 126.3 | 61.2 | #N/A | 67.9 | 60.2 | 106.8
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 5.55 | 4.49 | 7.03 | 9.76 | 4.66 | 6.01 | 6.08 | 7.82 | 7.64 | 5.77 | 7.68
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 9.05 | 4.37 | 5.76 | 5.69 | 8.01 | 7.13 | 5.67 | 7.49
CO2 emissions - 20% |  |  | 20 | 4.7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.54 | #N/A
CO2 emissions - 23% |  |  | 23 | #N/A | 3.96 | 6.0169 | 8.15 | 3.99 | 5.23 | 5.17 | 6.97 | 6.47 | 5.15 | 7.14
CO2 emissions - 30% |  |  | 30 | 4.42 | #N/A | 5.7259 | 7.58 | 3.79 | 4.93 | 4.87 | 6.94 | 6.05 | 4.98 | 6.9
CO2 emissions - 40% |  |  | 40 | #N/A | 3.41 | 5.2203 | 6.83 | 3.49 | 4.47 | 4.42 | 6.04 | 5.46 | 4.61 | 6.53
CO2 emissions - 50% |  |  | 50 | 3.6819 | #N/A | #N/A | 6.08 | 3.14 | 3.97 | 3.94 | 5.94 | 4.83 | 4.09 | 6.06
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 3.42 | 3.25 | #N/A | 4.17 | 3.66 | 5.49
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 8.1 | 3.48 | 12.22 | 10.05 | 9.62 | 7.14 | 6.85 | 9.6 | 7.74
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 4.24 | 12.54 | 10.25 | 10.07 | 7.09 | 7.39 | 10.54 | 7.78
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10.6 | #N/A
O2 emissions - 23% |  |  | 23 | #N/A | #N/A | 9.1448 | 5.17 | 12.94 | 10.82 | 10.61 | 8.03 | 8.04 | 11.23 | 7.93
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | 9.448 | 5.77 | 13.16 | 11.16 | 10.93 | 8.21 | 8.51 | 11.02 | 8.07
O2 emissions - 40% |  |  | 40 | #N/A | #N/A | 9.929 | 6.51 | 13.44 | 11.67 | 11.39 | 9.25 | 9.17 | 11.42 | 8.15
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | 7.16 | 13.77 | 12.18 | 11.85 | 9.23 | 9.78 | 12.13 | 8.34
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 12.73 | 12.74 | #N/A | 10.39 | 12.54 | 8.55
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | 265.05 | 2330.91 | #N/A | #N/A | #N/A | #N/A | 573.7771 | #N/A | 24.2397 | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.98 | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | 108.0912 | 938.1745 | #N/A | #N/A | #N/A | #N/A | 233.5507 | #N/A | 13.8451 | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | 66.2625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | 148.6297 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 1.6279 | 1.1986 | 2.3918 | 1.9178 | 1.8453 | 1.5152 | 1.4841 | 1.8421 | 1.5837
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 1.253 | 2.4823 | 1.9535 | 1.9213 | #N/A | 1.543 | 2.0076 | 1.5885
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.0192 | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | #N/A | #N/A | 1.7714 | 1.3266 | 2.6055 | 2.0629 | 2.0212 | 1.6191 | 1.6204 | 2.1494 | 1.6067
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | 1.8179 | 1.3789 | 2.6786 | 2.1341 | 2.0854 | #N/A | 1.6813 | 2.1042 | 1.6241
Air Excess (Lambda) - 40% |  |  | 40 | #N/A | #N/A | 1.8969 | 1.4493 | 2.7778 | 2.2508 | 2.1852 | 1.7872 | 1.7751 | 2.1921 | 1.6342
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | 1.5173 | 2.9046 | 2.381 | 2.2951 | #N/A | 1.8717 | 2.3675 | 1.6588
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 2.5393 | 2.5424 | #N/A | 1.9793 | 2.4823 | 1.6867
Qmin
|  | H2 | % | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A
H2 - 0% |  | %H2 in test gas | 0 | #N/A | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | 40 | #N/A | 10.2 | #N/A | 10.3 | 10 | #N/A | 11 | 10 | 10
H2 - 20% |  |  | 20 | 23 | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 20 | #N/A
H2 - 23% |  |  | 23 | #N/A | 40 | 23.1 | 23.1 | #N/A | 23.3 | 22.9 | #N/A | 23 | 23 | 23
H2 - 30% |  |  | 30 | 40 | 40 | #N/A | 30.3 | #N/A | 30.2 | 30.1 | #N/A | 29.8 | 30 | 30
H2 - 40% |  |  | 40 | #N/A | 40 | 39.9 | 40.3 | #N/A | 40.1 | 40.2 | #N/A | 39.9 | 40 | 40
H2 - 50% |  |  | 50 | 50 | 40 | #N/A | #N/A | #N/A | 50.2 | 49.9 | #N/A | 49.8 | 50 | 50
H2 - 60% |  |  | 60 | #N/A | 40 | #N/A | #N/A | #N/A | 59.9 | 59.7 | #N/A | #N/A | 60 | 60
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6604 | 45.7145 | 50.6061 | 50.6063 | #N/A | 50.6063 | 50.6063 | #N/A | 50.6063 | 50.6063 | 51.1359
Wobbe index - 10% |  |  | 10 | #N/A | 45.7145 | #N/A | 49.354 | #N/A | 49.3417 | 49.3787 | #N/A | 49.2555 | 49.3787 | 49.8196
Wobbe index - 20% |  |  | 20 | 47.8168 | 45.7145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 48.1467 | #N/A
Wobbe index - 23% |  |  | 23 | #N/A | 45.7145 | 47.551 | 47.7653 | #N/A | 47.7407 | 47.7899 | #N/A | 47.7776 | 47.7776 | 48.104
Wobbe index - 30% |  |  | 30 | 45.7405 | 45.7145 | #N/A | 46.8563 | #N/A | 46.8956 | 46.9078 | #N/A | 46.9444 | 46.92 | 47.1685
Wobbe index - 40% |  |  | 40 | #N/A | 45.7145 | 45.7263 | 45.6789 | #N/A | 45.7026 | 45.6907 | #N/A | 45.7263 | 45.7145 | 45.8554
Wobbe index - 50% |  |  | 50 | 44.5747 | 45.7145 | #N/A | #N/A | #N/A | 44.5354 | 44.569 | #N/A | 44.5802 | 44.5578 | 44.5833
Wobbe index - 60% |  |  | 60 | #N/A | 45.7145 | #N/A | #N/A | #N/A | 43.5097 | 43.5295 | #N/A | #N/A | 43.4999 | 43.3994
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 81.15 | #N/A | 91.4783 | 89.8394 | #N/A | 92.2 | 94.2 | #N/A | 95.33 | 97.92 | 95.1
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 89.6763 | #N/A | 92 | 94 | #N/A | 96 | 98.13 | 96
Efficiency (Hi) - 20% |  |  | 20 | 81.1456 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 97.87 | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | #N/A | 92.2326 | 89.9301 | #N/A | 91.9 | 94 | #N/A | 95.95 | 97.52 | 96.7
Efficiency (Hi) - 30% |  |  | 30 | 81.4845 | #N/A | #N/A | 90.2457 | #N/A | 91.9 | 94.2 | #N/A | 95.63 | 97.91 | 97.7
Efficiency (Hi) - 40% |  |  | 40 | #N/A | #N/A | 92.3171 | 90.6033 | #N/A | 92 | 94.7 | #N/A | 95.79 | 97.8 | 98.3
Efficiency (Hi) - 50% |  |  | 50 | 78.5489 | #N/A | #N/A | #N/A | #N/A | 92.4 | 94.7 | #N/A | 96.13 | 97.38 | 99
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 92.4 | 95 | #N/A | #N/A | 97.75 | 99.1
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 35.344 | #N/A | 8.6786 | 25 | #N/A | 43 | 74.3 | #N/A | 23.3 | 14.6079 | 545
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 25.5 | #N/A | 44.8 | 76.9 | #N/A | 28.4 | 15.5259 | 385
CO emissions - 20% |  |  | 20 | 34.3496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.6058 | #N/A
CO emissions - 23% |  |  | 23 | #N/A | #N/A | 8.4649 | 26.9 | #N/A | 47.1 | 76 | #N/A | 35.7 | 21.8393 | 325
CO emissions - 30% |  |  | 30 | 35.8882 | #N/A | #N/A | 27.3 | #N/A | 46.7 | 71.5 | #N/A | 37.4 | 19.4871 | 247
CO emissions - 40% |  |  | 40 | #N/A | #N/A | 10.0109 | 28.9 | #N/A | 45.7 | 70.8 | #N/A | 36.9 | 17.5475 | 219
CO emissions - 50% |  |  | 50 | 33.5884 | #N/A | #N/A | #N/A | #N/A | 43.9 | 67.1 | #N/A | 36.1 | 15.4838 | 215
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 43.3 | 117.2 | #N/A | #N/A | 15.5673 | 162
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | 116.3766 | #N/A | 7.2998 | 26.1 | #N/A | 17.8 | 96.4 | #N/A | 19.6 | 35.059 | 47
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 21.6 | #N/A | 14.1 | 94.9 | #N/A | 14.4 | 25.6178 | 47
NOx emissions - 20% |  |  | 20 | 94.5796 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21.7954 | #N/A
NOx emissions - 23% |  |  | 23 | #N/A | #N/A | 5.0034 | 17 | #N/A | 10.5 | 92.3 | #N/A | 10.2 | 16.6525 | 48
NOx emissions - 30% |  |  | 30 | 83.0318 | #N/A | #N/A | 15.1 | #N/A | 8.7 | 90.6 | #N/A | 8.5 | 14.1977 | 49
NOx emissions - 40% |  |  | 40 | #N/A | #N/A | 4.2204 | 12.7 | #N/A | 6.6 | 88.1 | #N/A | 7 | 8.7738 | 50
NOx emissions - 50% |  |  | 50 | 75.6921 | #N/A | #N/A | #N/A | #N/A | 5 | 85 | #N/A | 5.9 | 7.4322 | 57
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 3.7 | 78.9 | #N/A | #N/A | 8.4063 | 73
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 13.5551 | #N/A | 12.5798 | 10.5633 | #N/A | 12.261 | 14.3359 | #N/A | 9.4315 | 9.7334 | 30.23
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 10.248 | #N/A | 12.0783 | 13.9477 | #N/A | 8.8803 | 9.5593 | 30.2819
Qtest (input) - 20% |  |  | 20 | 12.7262 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.3765 | #N/A
Qtest (input) - 23% |  |  | 23 | #N/A | #N/A | 11.6959 | 9.8855 | #N/A | 12.0796 | 13.4666 | #N/A | 8.5482 | 9.1866 | 30.2506
Qtest (input) - 30% |  |  | 30 | 12.1014 | #N/A | #N/A | 9.6514 | #N/A | 12.0531 | 13.1808 | #N/A | 8.3626 | 9.1916 | 30.067
Qtest (input) - 40% |  |  | 40 | #N/A | #N/A | 11.248 | 9.3484 | #N/A | 12.0816 | 12.748 | #N/A | 8.0927 | 8.8209 | 30.1698
Qtest (input) - 50% |  |  | 50 | 11.9034 | #N/A | #N/A | #N/A | #N/A | 11.9981 | 12.3439 | #N/A | 7.7463 | 8.2741 | 30.216
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 12.0053 | 11.9243 | #N/A | #N/A | 7.8089 | 30.0368
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 82.14 | #N/A | 82.0507 | 73.1 | #N/A | 94.9 | 55.4 | #N/A | 61.9 | 53.5 | 54.3
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | 72.9 | #N/A | 95.2 | 55.2 | #N/A | 61.2 | 54.6 | 55.4
Flue gases temperatures - 20% |  |  | 20 | 80.87 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 51.6 | #N/A
Flue gases temperatures - 23% |  |  | 23 | #N/A | #N/A | 82.1419 | 72.2 | #N/A | 97.2 | 54.9 | #N/A | 60.4 | 54.2 | 56.5
Flue gases temperatures - 30% |  |  | 30 | 79.58 | #N/A | #N/A | 70.8 | #N/A | 98 | 54.7 | #N/A | 59.9 | 52.1 | 57.2
Flue gases temperatures - 40% |  |  | 40 | #N/A | #N/A | 80.8998 | 69.3 | #N/A | 99 | 54.5 | #N/A | 59.4 | 52.24 | 58.4
Flue gases temperatures - 50% |  |  | 50 | 76.2904 | #N/A | #N/A | #N/A | #N/A | 99.8 | 54.2 | #N/A | 58.9 | 56.7 | 59.8
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 100.6 | 53.9 | #N/A | #N/A | 50.68 | 60.8
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 2.7 | #N/A | 3.88 | 4.88 | #N/A | 3.77 | 2.91 | #N/A | 13.76 | 4.78 | 6.88
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 4.52 | #N/A | 3.52 | 2.74 | #N/A | 14.17 | 4.39 | 6.7
CO2 emissions - 20% |  |  | 20 | 2.54 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.15 | #N/A
CO2 emissions - 23% |  |  | 23 | #N/A | #N/A | 3.31 | 4.11 | #N/A | 3.24 | 2.5 | #N/A | 14.54 | 4 | 6.37
CO2 emissions - 30% |  |  | 30 | 2.2 | #N/A | #N/A | 3.87 | #N/A | 3.08 | 2.35 | #N/A | 14.75 | 3.82 | 6.31
CO2 emissions - 40% |  |  | 40 | #N/A | #N/A | 2.89 | 3.51 | #N/A | 2.85 | 2.15 | #N/A | 15.04 | 3.47 | 6.02
CO2 emissions - 50% |  |  | 50 | 2.0162 | #N/A | #N/A | #N/A | #N/A | 2.6 | 1.92 | #N/A | 15.33 | 3.08 | 5.52
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 2.32 | 1.67 | #N/A | #N/A | 2.81 | 5.08
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 13.994 | 11.66 | #N/A | 14.11 | 15.39 | #N/A | 3.7 | 12.47 | 9.18
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 12.06 | #N/A | 14.4 | 15.61 | #N/A | 3.39 | 13.03 | 9.23
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 13.25 | #N/A
O2 emissions - 23% |  |  | 23 | #N/A | #N/A | 14.6194 | 12.47 | #N/A | 14.69 | 15.88 | #N/A | 3.07 | 13.56 | 9.36
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | 12.73 | #N/A | 14.85 | 16.05 | #N/A | 2.88 | 13.39 | 9.2
O2 emissions - 40% |  |  | 40 | #N/A | #N/A | 15.0244 | 13.07 | #N/A | 15.03 | 16.26 | #N/A | 2.62 | 13.84 | 9.23
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 15.22 | 16.51 | #N/A | 2.33 | 14.54 | 9.57
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 15.41 | 16.74 | #N/A | #N/A | 14.68 | 9.67
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 1299.9008 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15.278 | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.0979 | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | 542.6696 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.2237 | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 2.9974 | 2.2484 | #N/A | 3.0479 | 3.7433 | #N/A | 1.2139 | 2.4619 | 1.7766
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 2.349 | #N/A | 3.1818 | 3.8961 | #N/A | 1.1925 | 2.6349 | 1.7842
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.7097 | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | #N/A | #N/A | 3.2912 | 2.4619 | #N/A | 3.3281 | 4.1016 | #N/A | 1.1712 | 2.8226 | 1.8041
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | 2.5393 | #N/A | 3.4146 | 4.2424 | #N/A | 1.1589 | 2.7595 | 1.7797
Air Excess (Lambda) - 40% |  |  | 40 | #N/A | #N/A | 3.5143 | 2.6482 | #N/A | 3.5176 | 4.4304 | #N/A | 1.1425 | 2.933 | 1.7842
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 3.6332 | 4.6771 | #N/A | 1.1248 | 3.2508 | 1.8373
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 3.7567 | 4.9296 | #N/A | #N/A | 3.3228 | 1.8535

## Seg200 Waterheaters
Do not touch this colum | THyGA Segment Seg200 waterheaters |  |  | THyGA Test data - Values | [5 empty] | Graph for the indicator (KPI): |  |  |  |  | Qtest (input)
|  |  |  | GA05 | GA09V03 | GA10v01 | GW14V01 | GW19 | EN04 |  | GA05 | GA09V03 | GA10v01 | GW14V01 | GW19 | EN04
| SEGMENT Nr |  |  | GA5_SEGM_201 | GA_SEGM_203 | GA10_SEGM_202 | GW14_SEGM_202 | GWI_19_SEGM_202
|  | Report test lab code |  | 201 | 203 | 202 | 202 | 202 | 50 | Qmax | Graph title | THyGA Segment Seg200 waterheaters - Qtest (input) at Qmax |  |  |  |  | Y axis | Power (kW)
|  | Appliance type code (B, CH, CO, F, WH,O) (*) |  | GA5 | GA | GA10 | GWI14 | GWI_19 |  | %H2 | GA05 | GA09 | GA10 | GW14 | GW19 | EN04
|  | Appliance type |  | WH | WH | WH | WH | WH | To DGC see Pdf file report sent | 0 | 10.9842 | 7.9134 | 19.0193 | 21.9754 | 28.6718 | 55.7705
[10 empty] | 10 | #N/A | #N/A | #N/A | 21.3718 | 28.751 | #N/A
|  | Burner type |  | Atmosperhic | Atmosperhic | Atmosperhic | atmospheric |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | For cooker hobs: burner tested? |  | NA | na | na |  |  | EN04_SEGM_204 | 23 | 10.3485 | 7.326 | 17.812 | 20.6752 | 28.1303 | 52.3664
|  | Modulating burner (Y/N) |  | N | N | Y | Y | Y | 204 | 30 | #N/A | #N/A | #N/A | 20.1451 | 27.6765 | #N/A
|  | Pressure regulator (Y/N) |  | N | N | Y | N | N | EN04 | 40 | 9.7186 | 6.9795 | 16.7822 | 19.6644 | 27.2176 | 49.0357
|  | Can the appliance be adjusted (Y/N) |  | N | N | N | N | N | CH | 50 | #N/A | #N/A | #N/A | 18.9353 | #N/A | #N/A
|  | Is the appliance equiped with a combustion control (Y/N) |  | N | N | N | N |  |  | 60 | #N/A | #N/A | #N/A | 18.1341 | #N/A | #N/A
|  | If the appliance can be adjusted. Instructions: |  | NA | N | na |  |  | Partial PreMix/Fanned
|  | If Yes what technology is used? |  | N | N | N
|  | Max. power input (net) [kW] |  | 10.5 | 7.7 | 26.2 | 22.6 | 30 | Y | Qmin | Graph title | THyGA Segment Seg200 waterheaters - Qtest (input) at Qmin |  |  |  |  | Y axis | Power (kW)
|  | Min. power input (net) [kW] |  | 5.3 | NA | 9 | 9.3 | 9.5 |  | %H2 | GA05 | GA09 | GA10 | GW14 | GW19 | EN04
|  | Flue type |  | Aas | B11BS | C12 |  |  | Y | 0 | 5.6598 | #N/A | 10.1238 | 8.7713 | 9.2429 | 18.2118
|  | Flue lenght |  | na | 1m | min length ( elbow 90°+ 0,8 m+Terminal) | 1m | 1 M | N | 10 | #N/A | #N/A | #N/A | 8.5967 | 9.1162 | #N/A
|  | Applicable standard(s) |  | EN26 | EN89 | EN26 |  |  | Y | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Gas category |  | I2E+ | I2E+ | I2E+ | II2ELL3P | II2HM3B/P |  | 23 | 5.2894 | #N/A | 9.6936 | 8.2316 | 9.1183 | 17.2593
|  | Origin of the appliance |  | Already used for other project | already used for another project | Already used for other project | New | New | 57 | 30 | #N/A | #N/A | #N/A | 8.2132 | 9.108 | #N/A
|  | Manufacture year |  | 2013 | 2018 | 2013 |  | 2021 | 13.5 | 40 | 5.0342 | #N/A | 8.3832 | 7.7377 | 9.0863 | 16.2207
[10 empty] | 50 | #N/A | #N/A | #N/A | 7.407 | #N/A | #N/A
[10 empty] | 60 | #N/A | #N/A | #N/A | 7.0716 | #N/A | #N/A
QMAX
H2
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | #N/A | #N/A | 10.2 | 10.1 | #N/A
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 23% |  |  | 23 | 23 | 22.8 | 23 | 22.9 | 23.2 | 23.09
H2 - 30% |  |  | 30 | #N/A | #N/A | #N/A | 30.3 | 29.9 | #N/A
H2 - 40% |  |  | 40 | 40 | 39.6 | 40 | 40.2 | 40.1 | 39.99
H2 - 50% |  |  | 50 | #N/A | #N/A | #N/A | 49.8 | #N/A | #N/A
H2 - 60% |  |  | 60 | #N/A | #N/A | #N/A | 60.2 | #N/A | #N/A
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 53.4706 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063
Wobbe index - 10% |  |  | 10 | #N/A | #N/A | 50.6063 | 49.354 | 49.3664 | #N/A
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | 50.4818 | 47.8022 | 47.7776 | 47.7899 | 47.753 | 47.7665
Wobbe index - 30% |  |  | 30 | #N/A | #N/A | #N/A | 46.8834 | 46.9322 | #N/A
Wobbe index - 40% |  |  | 40 | 48.3019 | 45.762 | 45.7145 | 45.6907 | 45.7026 | 45.7157
Wobbe index - 50% |  |  | 50 | #N/A | #N/A | #N/A | 44.5802 | #N/A | #N/A
Wobbe index - 60% |  |  | 60 | #N/A | #N/A | #N/A | 43.4803 | #N/A | #N/A
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 82.6 | #N/A | 84.1694 | 88.4 | 92.6694 | 102.0514
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 88.1 | 92.2751 | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | 82.6 | #N/A | 84.3279 | 87.8 | 92.3915 | 100.921
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | 87.8 | 92.208 | #N/A
Efficiency (Hi) - 40% |  |  | 40 | 82.5 | #N/A | 84.1291 | 87.9 | 92.7342 | 101.1957
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | #N/A | 88.4 | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | 89 | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 19.808 | 49.9194 | 27.9751 | 90.9 | 200.3 | 3.5146
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 79.1 | 189.6 | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | 10.2683 | 24.7409 | 27.6631 | 64.7 | 177 | 3.5989
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | 52.8 | 169 | #N/A
CO emissions - 40% |  |  | 40 | 8.5718 | 22.6785 | 24.6459 | 40.7 | 157.5 | 3.9825
CO emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | 36.1 | #N/A | #N/A
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | 27.6 | #N/A | #N/A
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | 118.4676 | 31.8504 | 87.2824 | 26.9 | 16.5 | 35.6995
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 19.8 | 14.6 | #N/A
NOx emissions - 23% |  |  | 23 | 105.1099 | 28.8644 | 94.6369 | 13.7 | 12 | 19.7873
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | 11.6 | 11.2 | #N/A
NOx emissions - 40% |  |  | 40 | 103.9652 | 25.8676 | 94.2345 | 8.7 | 10 | 12.4042
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | 8.3 | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | 6.4 | #N/A | #N/A
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 10.9842 | 7.9134 | 19.0193 | 21.9754 | 28.6718 | 55.7705
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 21.3718 | 28.751 | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | 10.3485 | 7.326 | 17.812 | 20.6752 | 28.1303 | 52.3664
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | 20.1451 | 27.6765 | #N/A
Qtest (input) - 40% |  |  | 40 | 9.7186 | 6.9795 | 16.7822 | 19.6644 | 27.2176 | 49.0357
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | #N/A | 18.9353 | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | 18.1341 | #N/A | #N/A
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 255.4 | 134.4 | 169.4 | 144.4 | 98.2 | 62.75
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | 142.3 | 99.3 | #N/A
Flue gases temperatures - 20% |  |  | 20 | 244.6 | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | 244.6 | 124.4 | 167.6 | 139.4 | 98.8 | 61.96
Flue gases temperatures - 30% |  |  | 30 | 240.3 | #N/A | #N/A | 138.3 | 98.2 | #N/A
Flue gases temperatures - 40% |  |  | 40 | 240.3 | 117.8 | 167.6 | 135.8 | 97.5 | 61.17
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | 139.7 | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | 137.6 | #N/A | #N/A
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 6.122 | 3.8 | 5.2 | 5.16 | 5.18 | 9.47
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 4.81 | 4.9 | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | 5.264 | 3.18 | 4.5 | 4.36 | 4.48 | 8.22
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | 4.09 | 4.26 | #N/A
CO2 emissions - 40% |  |  | 40 | 4.416 | 2.87 | 4.2 | 3.67 | 3.94 | 7.11
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | 3.51 | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | 3.06 | #N/A | #N/A
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | 11.54 | #N/A | 12.2 | 11.24 | 11.4 | 4.32
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 11.7 | 11.68 | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | 11.86 | #N/A | 12.1 | 12.17 | 12.13 | 5.72
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | 12.49 | 12.34 | #N/A
O2 emissions - 40% |  |  | 40 | 13.25 | #N/A | 12.1 | 12.94 | 12.61 | 6.87
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | 12.73 | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | 13.13 | #N/A | #N/A
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | 45.6004 | 24.5607 | 213.1534 | #N/A | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | 19.271 | #N/A | 74.5794 | #N/A | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | 9.9546 | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | 3.8074 | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 2.2199 | #N/A | 2.2308 | 2.1516 | 2.1875 | 1.259
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 2.2581 | 2.2532 | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | 2.2976 | #N/A | 2.4266 | 2.3783 | 2.3675 | 1.3743
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | 2.4677 | 2.4249 | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | 2.7097 | #N/A | 2.4162 | 2.6055 | 2.503 | 1.4862
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | 2.5393 | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | 2.6684 | #N/A | #N/A
Qmin
|  | H2 | %
H2 - 0% |  | %H2 in test gas | 0 | #N/A | 40 | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | 40 | 40 | 10 | 10.1 | #N/A
H2 - 20% |  |  | 20 | #N/A | 40 | 40 | #N/A | #N/A | #N/A
H2 - 23% |  |  | 23 | 23 | 40 | 23 | 23 | 23.1 | 23.06
H2 - 30% |  |  | 30 | #N/A | 40 | 40 | 29.8 | 30 | #N/A
H2 - 40% |  |  | 40 | 40 | 40 | 40 | 40.1 | 40.2 | 40.1
H2 - 50% |  |  | 50 | #N/A | 40 | 40 | 50.2 | #N/A | #N/A
H2 - 60% |  |  | 60 | #N/A | 40 | 40 | 59.9 | #N/A | #N/A
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6063 | 45.7145 | 50.6063 | 50.6063 | 50.6063 | 50.6063
Wobbe index - 10% |  |  | 10 | #N/A | 45.7145 | 45.7145 | 49.3787 | 49.3664 | #N/A
Wobbe index - 20% |  |  | 20 | #N/A | 45.7145 | 45.7145 | #N/A | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | 47.7776 | 45.7145 | 47.7776 | 47.7776 | 47.7653 | 47.7702
Wobbe index - 30% |  |  | 30 | #N/A | 45.7145 | 45.7145 | 46.9444 | 46.92 | #N/A
Wobbe index - 40% |  |  | 40 | 45.7145 | 45.7145 | 45.7145 | 45.7026 | 45.6907 | 45.7026
Wobbe index - 50% |  |  | 50 | #N/A | 45.7145 | 45.7145 | 44.5354 | #N/A | #N/A
Wobbe index - 60% |  |  | 60 | #N/A | 45.7145 | 45.7145 | 43.5097 | #N/A | #N/A
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 74.2 | #N/A | 77.0326 | 89 | 93.6 | 100.9039
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 88.5 | 93.4 | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | 73.7 | #N/A | 78.1962 | 88.5 | 93.1 | 104.5811
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | 88.1 | 92.7 | #N/A
Efficiency (Hi) - 40% |  |  | 40 | 73.5 | #N/A | 76.9399 | 88.7 | 92.9 | 105.6711
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | #N/A | 89.1 | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | 89.4 | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 53.6338 | #N/A | 160.2726 | 82 | 199.2 | 3.4177
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 93.2 | 181.5 | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | 58.8037 | #N/A | 156.1125 | 102.5 | 171.3 | 4.4131
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | 109.9 | 159.1 | #N/A
CO emissions - 40% |  |  | 40 | 66.506 | #N/A | 151.3184 | 61.4 | 151.6 | 5.0135
CO emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | 47.7 | #N/A | #N/A
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | 47.2 | #N/A | #N/A
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | 86.6196 | #N/A | #N/A | 14.3 | 35.2 | 26.4186
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 10.6 | 20.7 | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | 81.4177 | #N/A | #N/A | 7 | 12.6 | 13.7282
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | 5.3 | 10.2 | #N/A
NOx emissions - 40% |  |  | 40 | 73.7314 | #N/A | #N/A | 4.4 | 8.4 | 8.5635
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | 6 | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | 4.7 | #N/A | #N/A
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 5.6598 | #N/A | 10.1238 | 8.7713 | 9.2429 | 18.2118
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 8.5967 | 9.1162 | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | 5.2894 | #N/A | 9.6936 | 8.2316 | 9.1183 | 17.2593
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | 8.2132 | 9.108 | #N/A
Qtest (input) - 40% |  |  | 40 | 5.0342 | #N/A | 8.3832 | 7.7377 | 9.0863 | 16.2207
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | #N/A | 7.407 | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | 7.0716 | #N/A | #N/A
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 183.7 | #N/A | 128.4816 | 81.7 | 63.9 | 43.35
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | 79.9 | 65 | #N/A
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | 174.1 | #N/A | 128.3873 | 78.4 | 65.9 | 43.04
Flue gases temperatures - 30% |  |  | 30 | #N/A | #N/A | #N/A | 78.4 | 66.1 | #N/A
Flue gases temperatures - 40% |  |  | 40 | 170.3 | #N/A | 127.0465 | 77.8 | 66.8 | 43
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | 76.8 | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | 74.9 | #N/A | #N/A
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 3.424 | #N/A | 2.304 | 2.36 | 2.63 | 9.33
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 2.21 | 2.38 | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | 2.96 | #N/A | 1.9026 | 1.99 | 2.12 | 8.04
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | 1.85 | 1.99 | #N/A
CO2 emissions - 40% |  |  | 40 | 2.472 | #N/A | 1.8644 | 1.71 | 1.81 | 7
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | 1.53 | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | 1.31 | #N/A | #N/A
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | 15.54 | #N/A | #N/A | 16.32 | 16.13 | 4.63
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 16.48 | 16.48 | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | 15.83 | #N/A | #N/A | 16.73 | 16.85 | 5.94
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | 16.9 | 16.99 | #N/A
O2 emissions - 40% |  |  | 40 | 16.53 | #N/A | #N/A | 17.02 | 17.18 | 7.11
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | 17.15 | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | 17.41 | #N/A | #N/A
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 246.1725 | #N/A | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | 112.9661 | #N/A | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | 6.1918 | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 3.8462 | #N/A | #N/A | 4.4872 | 4.3121 | 1.2828
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 4.646 | 4.646 | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | 4.0619 | #N/A | #N/A | 4.918 | 5.0602 | 1.3944
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | 5.122 | 5.2369 | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | 4.698 | #N/A | #N/A | 5.2764 | 5.4974 | 1.5119
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | 5.4545 | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | 5.8496 | #N/A | #N/A

## Seg300 domestic cookers
Do not touch this colum | THyGA Segment Seg300 domestic cookers |  |  | THyGA Test data - Values | [31 empty] | Graph for the indicator (KPI): |  |  |  |  | CO emissions
[32 empty] | they were appart? |  |  | They were appart?
|  |  |  | D1 | D2c | D7v02 | D8v02 | EB10v03 | EN05v03 | EN06v04 | EN10v03 | EB07V03 | EB08v04 | EB09v03 | EB11v03 | BS01 | BS02 | EN07v04 | EN09v04 | EB15V03 | EB16V03 | AP01V01 | EN13 | EN14 | EN15 | EN16 | EN22 | EN08v04 | EN11V02 | EN12aV02 | EN12bV02 | D3 | D9v02 | D10v02 |  |  | D1 | D2c | D7v02 | D8v02 | EB10v03 | EN05v03 | EN06v04 | EN10v03 | EB07V03 | EB08v04 | EB09v03 | EB11v03 | BS01 | BS02 | EN07v04 | EN09v04 | EB15V03 | EB16V03 | AP01V01 | EN13 | EN14 | EN15 | EN16 | EN22 | EN08v04 | EN11V02 | EN12aV02 | EN12bV02 | D3 | D9v02 | D10v02
| SEGMENT Nr |  |  | D1_SEGM_301 | D2_SEGM_301 | D7_SEGM_301 | D8_SEGM_301 | EB10_SEGM_301 | EN05_SEGM_301 | EN06_SEGM_301 | EN10_SEGM_301 | EB07_SEGM_301 & 302 | EB08_SEGM_303 | EB09_SEGM_303 | EB09_SEGM_303 | BSH_SEGM_303 | BSH_SEGM_303 | EN07_SEGM_303 | EN09_SEGM_303 | EB15_SEGM_304 | EB16_SEGM_304 | A+_SEGM_302 | EN13_SEGM_301 | EN14_SEGM_301 | EN15_SEGM_311 | EN16_SEGM_309 | EN22_SEGM_301 | EN08_SEGM_301 | EN11_SEGM_301 | EN12b_SEGM_301 | EN12b_SEGM_301 | D3_SEGM_301 | D9_SEGM_311 | D10_SEGM_311
|  | Report test lab code |  | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 | 301 & 302 | 303 | 303 | 303 | 303 | 303 | 303 | 303 | 304 | 304 | 302 | 301 | 301 | 311 | 309 | 301 | 301 | 301 | 301 | 301 | 301 | 311 | 311 |  | Qmax | Graph title | THyGA Segment Seg300 domestic cookers - CO emissions at Qmax | [5 empty] | Y axis | CO emissions (ppm)
|  | Appliance type code (B, CH, CO, F, WH,O) (*) |  | D1 | D2 | D7 | D8 | EB10 | EN05 | EN06 | EN10 | EB07 | EB08 | EB09 | EB11 | BSH | BSH | EN07 | EN09 | EB15 | EB16 | A+ | EN13 | EN14 | EN15 | EN16 | EN22 | EN08 | EN11 | EN12b | EN12b | D3 | D9 | D10 |  | %H2 | D1 | D2c | D7v0 | D8v0 | EB10 | EN05 | EN06 | EN10 | EN15 | EN16 | EN22 | EN08 | EN11 | EN12 | EN12 | D3 | D9v0 | D10v | EB07 | EB08 | EB09 | EB11 | BS01 | BS02 | EN07 | EN09 | EB15 | EB16 | AP01 | EN13 | EN14
|  | Appliance type |  | C | C | CH | Freestanding cooker. Gas hob | CH | CH | CH | CH | CH | CH | CH | CH | Cookers Hobs | Cookers Hobs | ch | CH | C | C | C | CH | CH | CH | CH | CH | CH | CH | CH | CH | CO | CO | CO |  | 0 | 184.5861 | 49.2499 | 908.7275 | 470.7961 | 29 | 89.3861 | 393.0659 | 126.2574 | 199.6595 | 29.9154 | 274.9653 | 28.6571 | 222.6543 | 239.1779 | 455.8877 | 125.1019 | 145.4707 | 280.3617 | 37 | 224 | 61 | 25 | 423.4726 | 314.4518 | 545.6647 | 268.4486 | 316.6495 | 47.664 | 321.6913 | 77.1644 | 27.3827
|  |  |  | EN30 free standing cooker with partialy aerated ribbon burner (oven) ”atmospheric Partially Aerated Single Ring burner” (hob) | EN30 free standing cooker with partialy aerated ribbon burner (oven) ”atmospheric Partially Aerated Single Ring burner” (hob) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Oven | 0 | 0 | 0 | 0 | 0 | EN30 free standing cooker with partialy aerated ribbon burner (oven) ”atmospheric Partially Aerated Single Ring burner” (hob) | 0 | Top oven burner (grill) |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 338.2413 | 219.8671 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Burner type |  | See above | See above | Surf. atmospheric burner (large) | Surface atmospheric burner | venturi burner (High Output) | Partially premixed atmospheric burner | Atmospheric burner | Partially premixed atmospheric burner | Atmospheric burner (Standard Output Burner) | Atmospheric multi ring burner (dual wok burner) | Venturi multi ring burner (dual wok burner) | venturi burner (Economy) | Atmospheric burner | Venturi type burner | Partially premixed atmospheric burner | Partially premixed atmospheric burner | Horizontal venturi burner | Horizontal venturi burner | open | Open burner | Open burner | Flame sheet | Tubular cavity burner | Open burner | SPECIFIC DESIGN (Atmospheric burner) | Venturi vertical flame burner | Venturi vertical flame burner | Venturi vertical flame burner | See above | Cavity burner "metal sheet" | Cavity burner "metal sheet" with deflector |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 110.0055 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | For cooker hobs: burner tested? |  | The bigest one | The smallest one | Front Left (largest burner) | Back left | 0 | B1 - Auxiliary | Rapid burner B3 | B1 - Auxiliary | 0 | 0 | 0 | 0 | Double crown dual wok burner (5kW) | Double crown dual wok burner (6kW) | B4 - Multi Ring | B4 - Multi Crown | 0 | 0 | 120mm diameter | Rapid | Auxiliary | Grill | Oven | Multiring Wok burner | Bridge burner | Rapid burner | Auxiliary burner | Auxiliary burner | OVEN | Oven | Oven |  | 23 | #N/A | #N/A | 593.5806 | 311.2098 | 3 | 40.884 | 165.4918 | 69.5342 | 194.729 | 29.7001 | 153.6491 | 69.3828 | 168.6324 | #N/A | 362.6868 | #N/A | 121.0786 | #N/A | 19.701 | 37 | 13 | 9 | 207.6742 | 121.3294 | 119.7147 | 130.0682 | 6.5888 | 27.171 | 92.3495 | 27.0998 | 11.4043
|  | Modulating burner (Y/N) |  | N | N | N | N | N | n | n | n | N | N | N | N | N | N | n | n | N | N | N | Y | Y | N | Y | Y | n | n | n | n | N | N | N |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 92.7851 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 178.9944 | 84.0407 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Pressure regulator (Y/N) |  | N | N | N | N | N | n | n | n | N | N | N | N | N | N | [18 empty] | 40 | #N/A | #N/A | 443.6269 | 266.3936 | 1 | 21.4589 | 64.7986 | 38.1538 | 196.8786 | 35.3341 | 54.4153 | 47.6815 | 53.9062 | #N/A | 240.464 | 88.8115 | 83.7455 | 476.1908 | #N/A | 5 | #N/A | 3 | 125.0156 | 74.9205 | 41.2432 | 39.0641 | 11.4816 | 70.9044 | 32.3171 | 12.3844 | 12.3771 | bar: ch to CO
|  | Can the appliance be adjusted (Y/N) |  | N | N | N | N | N | n | n | n | N | N | N | N | N | N | n | n | N | N | Only minimum power input | N | N | N | N | N | n | n | n | n | N | N | N |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 72.8593 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 81.7544 | 51.1618 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Is the appliance equiped with a combustion control (Y/N) |  | N | N | N | N | N | 0 | 0 | 0 | N | N | N | N | N | N | 0 | 0 | N | N | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N |  | 60 | 20.5654 | 26.9236 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.9862 | #N/A | #N/A
|  | If the appliance can be adjusted. Instructions: |  | #REF! | #REF! | NR | Nor relevant | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | 0 | 0 | 0 | 0 | Screw in the valve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N
|  | If Yes what technology is used? |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0
|  | Max. power input (net) [kW] |  | 3 | 1 | 2.7027 | 0.9009 | 2.8 | 1 | 2.95 | 1 | 1.75 | 5 | 6.1 | 1.1 | 10.75 | 11.8 | 1.4 | 4 | 2.9 | 1 | 6.8 | 3 | 1.0 | 2.73 | 2.5 | 4 | 3.7 | 2.9 | 1 | 1 | 2.5 | 2.4324 | 1.7117 |  | Qmin | Graph title | THyGA Segment Seg300 domestic cookers - CO emissions at Qmin | [5 empty] | Y axis | CO emissions (ppm)
|  | Min. power input (net) [kW] |  | 0.76 | 0.48 | 0.67568 | 0.31532 | 0.6 | 0.33 | 0.75 | 0.33 | 0.41 | 0.3 | 0.3 | 0.33 | 1.64 | 1.64 | 4 | 1.4 | 1.2 | 0.5 | 2 | Not mentionned in product documentation | Not mentionned in product documentation | Not mentionned in product documentation | Not mentionned in product documentation | Not mentionned in product documentation | 1.2 | 1.2 | 0.5 | 0.5 | 1 | 0.81081 | not relevant |  | %H2 | D1 | D2c | D7v0 | D8v0 | EB10 | EN05 | EN06 | EN10 | EN15 | EN16 | EN22 | EN08 | EN11 | EN12 | EN12 | D3 | D9v0 | D10v | EB07 | EB08 | EB09 | EB11 | BS01 | BS02 | EN07 | EN09 | EB15 | EB16 | AP01 | EN13 | EN14
|  | Flue type |  | na | na | not relevant | not relevant | 0 | Type A | Type A appliance | Type A | 0 | 0 | 0 | 0 | 0 | 0 | Type A | Type A | NA | NA | Type A | A | A | A | A | A | Type A appliance | type A | type A | type A | na | not relevant | not relevant |  | 0 | 226.9343 | 105.409 | 246.4445 | 372.405 | 95 | 61.6507 | 216.9506 | 134.5747 | 291.2817 | 82.9168 | 37.4697 | 665.0089 | 239.1779 | #N/A | 86.8073 | 593.276 | 1847.4778 | #N/A | 594 | 36 | 218 | 122 | #N/A | #N/A | 172.8407 | 10.9937 | 86.1801 | 98.9232 | 568.3506 | 279.611 | 445.5396
|  | Flue lenght |  | na | na | not relevant | not relevant | NA | NR | 0 | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | na | not relevant | not relevant |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Applicable standard(s) |  | EN30 | EN30 | EN 30-1-1:2008+A3:2013 E | EN 30-1-1:2008+A3:2013 E | EN 30-1-1, EN30-2-1 | EN30-1 | EN 30 | EN30-1 | EN 30-1-1, EN30-2-1 | EN 30-1-1, EN30-2-1 | EN 30-1-1, EN30-2-1 | EN 30-1-1, EN30-2-1 | EN 30-1-1:2008+A3:2013; EN 30-2-1:2015 | EN 30-1-1:2008+A3:2013; EN 30-2-1:2015 | EN30-1 | EN30-1 | EN 30 | EN 30 | EN203 | EN30 | EN30 | EN30 | EN30 | EN30 | EN 30 | EN30 | EN30 | EN30 | EN30 | EN 30-1-1:2008+A3:2013 E | EN 30-1-1:2008+A3:2013 E |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 891.8075 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Gas category |  | III 2H3B/P | III 2H3B/P | II 2H3B/P | II 2H3B/P | II 2ELL3B/P | E+ | E+ | E+ | II 2ELL3B/P | II 2ELL3B/P | II 2ELL3B/P | II 2ELL3B/P | 2H3B/P | 2H3B/P | E+ | E+ | II2H3B/P | II2H3B/P | II2H3P | II2H3+ | II2H3+ | II2H3+ | II2H3+ | II2H3+ | E+ | I2E+ | I2E+ | I2E+ | III 2H3B/P | II 2H3B/P | II 2H3B/P |  | 23 | #N/A | #N/A | 194.127 | 561.5816 | 214 | 223.5725 | 173.865 | 252.9484 | 472.1685 | 86.3292 | 45.6989 | 510.4394 | 70.3319 | #N/A | 112.9073 | #N/A | 1930.3383 | #N/A | 486 | 32 | 393 | 135 | #N/A | #N/A | 158.2796 | 229.8226 | 58.2628 | 76.8698 | 585.275 | 401.642 | 735.7759
|  | Origin of the appliance |  | Bought new in a shop 2020 | Bought new in a shop 2020 | sent by manufacturer | Electrolux Appliance AB, Krakow, Poland | Spain | Manufacturer | italy | Manufacturer | Spain | Spain | Spain | Spain | Production | Production | Manufacturer | Manufacturer | Italy | Italy | Production (brand new) | Manufacturer (UK) | Manufacturer (UK) | Manufacturer (UK) | Manufacturer (UK) | Manufacturer (UK) | italy | Manufacturer | Manufacturer | Manufacturer | Bought new in a shop 2020 | sent by manufacturer | sent by manufacturer |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1055.7825 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Manufacture year |  | Not known | Not known | 2019 | 2019 | 2021 | 0 | recent | 0 | 2021 | 2021 | 2021 | 2021 | 2021 | 2021 | 0 | 0 | 2021 | 2021 | 2021 | 2020 | 2020 | 2020 | 2020 | 2020 | recent |  | 0 | 0 | Not known | 2019 | 2019 |  | 40 | #N/A | #N/A | 202.9666 | 642.7275 | 250 | 514.9852 | 182.4236 | 288.4255 | 616.3964 | 79.4622 | 58.9014 | 788.9734 | 51.8086 | #N/A | 165.4749 | 951.2437 | 1921.9712 | #N/A | 459 | 68 | 478 | 250 | #N/A | #N/A | 172.5648 | 249.4024 | 69.0111 | 199.8673 | 611.9871 | 609.7349 | 986.2006
[18 empty] | CO: turns on/off automatically because of the thermostat, strange results |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 839.5001 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[36 empty] | 60 | 188.4087 | 112.6367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 802.4258 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 486.5988 | #N/A | #N/A
QMAX
H2
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | #N/A | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 23 | #N/A | #N/A
H2 - 23% |  |  | 23 | #N/A | #N/A | 23 | 23 | 23.2 | 23.36 | 23.22 | 22.91 | 23 | 23 | 23.5 | 22.6 | 23 | 23 | 23.2 | 23.1 | 23 | 23 | 25.08 | 23 | 23 | 23 | 23 | 23 | 23.01 | 23 | 23 | 23 | #N/A | 23.59 | #N/A
H2 - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 30 | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 30 | #N/A | #N/A
H2 - 40% |  |  | 40 | #N/A | #N/A | 40 | 40 | 39.6 | 40 | 39.7463 | 40 | 40 | 40 | 39.9 | 40.6 | 40 | 40 | 40 | 40 | 40 | 40 | 39.32 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 41.79 | 40
H2 - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 50 | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 50 | #N/A | #N/A
H2 - 60% |  |  | 60 | 58 | 61.56 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 62 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 60 | #N/A | #N/A
|  | Wobbe index | [MJ/m³]
Wobbe index - 0% |  | %H2 in test gas | 0 | 53.4425 | 53.4425 | 53.4425 | 50.5796 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 53.4706 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.5716 | 50.6063 | 50.6063 | 50.6063 | 50.6604 | 53.4425 | 53.4425
Wobbe index - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 50.6063 | #N/A | #N/A | 49.3787 | 49.3787 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 47.8168 | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | #N/A | #N/A | 50.4427 | 47.7405 | 47.753 | 47.7333 | 47.7505 | 47.7886 | 47.7776 | 47.7776 | 47.7161 | 47.8268 | 47.7776 | 47.7776 | 47.753 | 47.7653 | 47.7776 | 47.7776 | 50.2118 | 47.7776 | 47.7776 | 47.7776 | 47.7776 | 47.7776 | 47.7763 | 47.7776 | 47.7776 | 47.7776 | #N/A | 50.3657 | #N/A
Wobbe index - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 46.92 | 46.92 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 40% |  |  | 40 | #N/A | #N/A | 48.2523 | 45.6675 | 45.762 | 45.7145 | 45.7446 | 45.6552 | 45.7145 | 45.7145 | 45.7263 | 48.3327 | 45.7145 | 45.7145 | 45.7145 | 45.6683 | 45.7145 | 45.7145 | 48.2945 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7405 | 48.0274 | 48.2523
Wobbe index - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44.5578 | 44.5578 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44.5747 | #N/A | #N/A
Wobbe index - 60% |  |  | 60 | 46.1088 | 45.7344 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 45.7586 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 43.5063 | #N/A | #N/A
|  | Efficiency (Hi) | % on Hi
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 52.1 | #N/A | 58.4 | 61.5 | #N/A | #N/A | 58.1569 | #N/A | 56.7 | #N/A | 46.77 | #N/A | 52.7273 | 54.717 | 56.0345 | 55.7814 | #N/A | #N/A | #N/A | 59.9131 | #N/A | 59.9131 | #N/A | #N/A | 54.5533 | 61.8893 | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 52.7273 | 53.7037 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | #N/A | 59.1 | #N/A | #N/A | #N/A | 61.3101 | #N/A | 57.45 | #N/A | 48.8 | #N/A | 52.7273 | 53.7037 | 55.8418 | 55.8418 | #N/A | #N/A | #N/A | 59.7571 | #N/A | 59.7571 | #N/A | #N/A | 53.9174 | 61.0539 | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 51.7857 | 54.717 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 40% |  |  | 40 | #N/A | #N/A | 60.4 | 63.8 | #N/A | #N/A | 61.4977 | #N/A | 61.19 | #N/A | 49.03 | #N/A | 50.8772 | 52.7273 | 50.9127 | #N/A | #N/A | #N/A | #N/A | 59.6192 | #N/A | 59.6192 | #N/A | #N/A | 53.8148 | 59.477 | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 50.8772 | 53.7037 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | 51.8 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm
CO emissions - 0% |  | %H2 in test gas | 0 | 184.5861 | 49.2499 | 908.7275 | 470.7961 | 29 | 89.3861 | 393.0659 | 126.2574 | 37 | 224 | 61 | 25 | 423.4726 | 314.4518 | 545.6647 | 268.4486 | 316.6495 | 47.664 | 321.6913 | 77.1644 | 27.3827 | 199.6595 | 29.9154 | 274.9653 | 28.6571 | 222.6543 | 239.1779 | 455.8877 | 125.1019 | 145.4707 | 280.3617
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 338.2413 | 219.8671 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 110.0055 | #N/A | #N/A
CO emissions - 23% |  |  | 23 | #N/A | #N/A | 593.5806 | 311.2098 | 3 | 40.884 | 165.4918 | 69.5342 | 19.701 | 37 | 13 | 9 | 207.6742 | 121.3294 | 119.7147 | 130.0682 | 6.5888 | 27.171 | 92.3495 | 27.0998 | 11.4043 | 194.729 | 29.7001 | 153.6491 | 69.3828 | 168.6324 | #N/A | 362.6868 | #N/A | 121.0786 | #N/A
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 178.9944 | 84.0407 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 92.7851 | #N/A | #N/A
CO emissions - 40% |  |  | 40 | #N/A | #N/A | 443.6269 | 266.3936 | 1 | 21.4589 | 64.7986 | 38.1538 | #N/A | 5 | #N/A | 3 | 125.0156 | 74.9205 | 41.2432 | 39.0641 | 11.4816 | 70.9044 | 32.3171 | 12.3844 | 12.3771 | 196.8786 | 35.3341 | 54.4153 | 47.6815 | 53.9062 | #N/A | 240.464 | 88.8115 | 83.7455 | 476.1908
CO emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 81.7544 | 51.1618 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 72.8593 | #N/A | #N/A
CO emissions - 60% |  |  | 60 | 20.5654 | 26.9236 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.9862 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | NOx emissions | ppm
NOx emissions - 0% |  | %H2 in test gas | 0 | 78.8774 | 74.0755 | 71.8068 | 68.768 | #N/A | 65.7975 | 59.6921 | 75.2771 | #N/A | #N/A | #N/A | #N/A | 66.1872 | 94.0417 | 76.3562 | 84.4976 | 40.1038 | 21.7776 | 73.7998 | 79.3691 | 59.1467 | 18.0241 | 86.3491 | 72.8941 | 79.8194 | 53.2761 | 30.7661 | 47.2638 | 77.9085 | 75.6448 | 68.768
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 63.5 | 95.2758 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 69.2487 | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | #N/A | #N/A | 69.9977 | 65.5179 | #N/A | 66.2784 | 60.395 | 68.5231 | #N/A | #N/A | #N/A | #N/A | 62.3023 | 91.7748 | 79.1665 | 82.9648 | 22.2705 | 12.1687 | 73.3936 | 75.0825 | 56.4514 | 19.4563 | 71.3576 | 78.5839 | 53.2314 | 39.7822 | #N/A | 37.185 | #N/A | 66.5932 | #N/A
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 63.1745 | 93.0912 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 40% |  |  | 40 | #N/A | #N/A | 63.7895 | 63.4271 | #N/A | 63.3014 | 63.6393 | 65.8408 | #N/A | #N/A | #N/A | #N/A | 61.037 | 93.6507 | 78.1178 | 80.0765 | 25.7309 | 27.0023 | 63.557 | 72.2423 | 55.4262 | 16.9556 | 57.093 | 80.1513 | 57.4906 | 32.0091 | #N/A | 29.4606 | 61.2835 | 50.2473 | 58.548
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 59.9532 | 89.5331 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 56.1116 | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | 73.7251 | 45.8603 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 52.8682 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 53.9949 | #N/A | #N/A
|  | Qtest (input) | kW
Qtest (input) - 0% |  | %H2 in test gas | 0 | 2.7719 | 0.89807 | 2.7774 | 0.84078 | 2.3107 | 0.83801 | 2.5248 | 0.85305 | 1.5279 | 3.8009 | 4.9515 | 0.91486 | 4.3846 | 5.4943 | 3.2032 | 3.359 | 2.3767 | 0.94787 | 6.3521 | 2.5069 | 0.78904 | 2.0719 | 1.4142 | 3.5448 | 2.9754 | 2.273 | 0.9322 | 0.86695 | 2.5225 | 2.3822 | #N/A
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.2117 | 5.313 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.6329 | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | #N/A | #N/A | 2.5793 | 0.75567 | 2.1019 | 0.78245 | 2.3401 | #N/A | 1.4089 | 3.6092 | 4.5716 | 0.8259 | 4.0747 | 5.0595 | 2.9387 | 3.0853 | 2.1924 | 0.87935 | 5.7167 | 2.235 | 0.74809 | 1.9147 | 1.356 | 3.2629 | 2.7406 | 2.1018 | #N/A | 0.7912 | #N/A | 1.5314 | #N/A
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.9685 | 4.9311 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 40% |  |  | 40 | #N/A | #N/A | 2.4425 | 0.71189 | 1.9711 | 0.73183 | 2.2665 | 0.7518 | 1.2909 | 3.3562 | 4.3252 | 0.83904 | 3.8284 | 4.8831 | 2.8173 | 2.8694 | 1.8412 | 0.78743 | 5.4873 | 2.1829 | 0.70306 | 1.8367 | 1.2953 | 3.0891 | 2.6312 | 1.9892 | #N/A | 0.74123 | 1.6958 | 2.095 | #N/A
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.6887 | 4.5052 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.6622 | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | 2.3315 | 0.64446 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.7684 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.8158 | #N/A | #N/A
|  | Flue gases temperatures | [°C]
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 242 | 248 | 205.84 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 196.94 | #N/A | #N/A | #N/A | #N/A | 90.84 | #N/A | 215 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 217 | #N/A
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | #N/A | #N/A | 266 | 266 | 186.49 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 180.85 | #N/A | #N/A | #N/A | #N/A | 114.8 | #N/A | 210 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 220 | #N/A
Flue gases temperatures - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 40% |  |  | 40 | #N/A | #N/A | 262 | 283 | 188.81 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 161.92 | #N/A | #N/A | #N/A | #N/A | 116.2 | #N/A | 249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 225 | #N/A
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 210 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO2 emissions | [%]
CO2 emissions - 0% |  | %H2 in test gas | 0 | 3.6 | 1.8964 | 4.7 | 2.2 | 6.8 | 2.6 | 5.03 | 2.4869 | 3.72 | 2.26 | 4.1 | 4.25 | 3.71 | 3.96 | 6.114 | 5.0881 | 6.4 | 2.2064 | 2.46 | 3.695 | 2.125 | 2.1906 | 2.1749 | 5.955 | 0.52328 | 3.6693 | 2.3539 | 2.1684 | 2.5524 | 2 | 2.2
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.56 | 3.72 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.1945 | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | #N/A | #N/A | 3.9 | 2 | 5.62 | 2.07 | 4.13 | 2.2038 | 2.8139 | 1.9 | 3.41 | 3.83 | 3.26 | 3.51 | 4.8892 | 4.855 | 4.97 | 1.9735 | 2.23 | 3.425 | 1.915 | 1.8559 | 1.9397 | 4.655 | 0.48 | 3.1932 | #N/A | 1.9137 | #N/A | 1.8 | #N/A
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.03 | 3.29 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 40% |  |  | 40 | #N/A | #N/A | 3.5 | 1.6 | 4.57 | 1.8689 | 3.4234 | 1.8428 | 2.2136 | 1.64 | 2.93 | 3.25 | 2.76 | 2.98 | 3.9018 | 3.8572 | 4.78 | 2.6966 | 1.89 | 2.95 | 1.6399 | 1.6238 | 1.6444 | 4.1306 | 0.42567 | 2.79 | #N/A | 1.6694 | 1.9687 | 1.8 | 1.3
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.45 | 2.61 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.7975 | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | 2.3 | 1.1373 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.49 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.7494 | #N/A | #N/A
|  | O2 emissions | [%]
O2 emissions - 0% |  | %H2 in test gas | 0 | 14.5 | 17.5497 | 12.7 | 17.1 | #N/A | 16.53 | 12.34 | 16.5715 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.9658 | 12.0003 | 10.96 | 17.7557 | 15.94 | 14.22 | 17.11 | 16.887 | 16.9934 | 10.405 | 19.9805 | 14.3689 | 16.7213 | 17.0064 | 16.3887 | 17.5 | 17.2
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 16.752 | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | #N/A | #N/A | 13.5 | 17.4 | #N/A | 16.84 | 13.11 | 16.8295 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.8682 | 11.855 | 11.93 | 18.6748 | 17.18 | 14.46 | 17.37 | 17.3206 | 17.2641 | 11.915 | 20.03 | 14.7854 | #N/A | 17.252 | #N/A | 17.7 | #N/A
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 40% |  |  | 40 | #N/A | #N/A | 13.9 | 17.6 | #N/A | 17.26 | 14.1831 | 17.1555 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 13.0938 | 13.227 | 12.61 | 18.2395 | 17.68 | 14.995 | 17.5843 | 17.4777 | 17.5371 | 12.3634 | 20.016 | 15.19 | #N/A | 17.4172 | 16.9048 | 17.5 | 18.4
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 17.0047 | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | 15.6 | 18.2922 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 16.7647 | #N/A | #N/A
|  | Unburnt UHC emissions | ppm
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 334.1154 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 39.668 | 99.4299 | #N/A | 2.4096 | 1.9865 | 182.1694 | 83.1769 | 3.5941 | #N/A | 155.0733 | 218.2918 | 218.2918 | #N/A | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.8074 | 2.1956 | #N/A | 138.5794 | 4.2894 | #N/A | 229.4033 | 224.6252 | 224.6252 | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 522.8665 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 34.7222 | 59.4678 | #N/A | 1.7645 | 1.7602 | 154.4599 | 89.3304 | 1.9515 | #N/A | 160.8663 | 255.7285 | 255.7285 | #N/A | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 63.6859 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda)
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 3.2308 | 6.0864 | 2.5301 | 5.3846 | #N/A | 4.698 | 2.4249 | 4.7421 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.9032 | 2.3334 | 2.0916 | 6.4729 | 4.1502 | 3.0973 | 5.3985 | 5.1057 | 5.2413 | 1.9821 | 20.5993 | 3.1669 | 4.9081 | 5.2584 | 4.554 | 6 | 5.5263
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.9435 | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | #N/A | #N/A | 2.8 | 5.8333 | #N/A | 5.0481 | 2.6616 | 5.0354 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.2997 | 2.2963 | 2.3153 | 9.0315 | 5.4974 | 3.211 | 5.7851 | 5.7074 | 5.6211 | 2.3115 | 21.6495 | 3.3792 | #N/A | 5.603 | #N/A | 6.3636 | #N/A
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | #N/A | #N/A | 2.9577 | 6.1765 | #N/A | 5.6149 | 3.0806 | 5.4624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.6562 | 2.7017 | 2.503 | 7.6073 | 6.3253 | 3.4971 | 6.148 | 5.962 | 6.0643 | 2.4315 | 21.3419 | 3.6145 | #N/A | 5.8614 | 5.128 | 6 | 8.0769
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.2562 | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | 3.8889 | 7.7553 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7.2414 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.9583 | #N/A | #N/A
Qmin
|  | H2 | %
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.8724 | #N/A | #N/A
H2 - 23% |  |  | 23 | #N/A | #N/A | 23 | 23 | 22.1 | 23.21 | 23.17 | 23.0343 | 23 | 23 | 22.6 | 24.2 | 40 | #N/A | 23.1 | 23.01 | 23 | 23 | 25.1 | 23 | 23 | 23 | 23 | 23 | 22.9949 | 23 | 23.1 | 23.1 | #N/A | 23.59 | #N/A
H2 - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 29.7468 | #N/A | #N/A
H2 - 40% |  |  | 40 | #N/A | #N/A | 40 | 40 | 40.3 | 39.799 | 39.8067 | 40.1249 | 40 | 40 | 40.8 | 40.6 | 40 | #N/A | 39.9458 | 40.11 | 40 | 40 | 40.48 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39.9267 | 39.9267 | 39.8768 | 40.6 | #N/A
H2 - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 50 | #N/A | #N/A
H2 - 60% |  |  | 60 | 58 | 61.56 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | 63.6 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 60 | #N/A | #N/A
|  | Wobbe index | [MJ/m³]
Wobbe index - 0% |  | %H2 in test gas | 0 | 53.4425 | 53.4425 | 50.5796 | 50.5796 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 45.7145 | #N/A | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6604 | 50.5796 | #N/A
Wobbe index - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 45.7145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 45.7145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 47.8326 | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | #N/A | #N/A | 47.7405 | 47.7405 | 47.8883 | 47.7518 | 47.7567 | 47.7734 | 47.7776 | 47.7776 | 47.8268 | 47.6301 | 45.7145 | #N/A | 47.7653 | 47.7763 | 47.7776 | 47.7776 | 47.5277 | 47.7776 | 47.7776 | 47.7776 | 47.7776 | 47.7776 | 47.7782 | 47.7776 | 47.7653 | 47.7653 | #N/A | 47.6677 | #N/A
Wobbe index - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 45.7145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 46.9851 | #N/A | #N/A
Wobbe index - 40% |  |  | 40 | #N/A | #N/A | 45.6675 | 45.6675 | 45.6789 | 45.7383 | 45.7374 | 45.6997 | 45.7145 | 45.7145 | 45.6197 | 48.3327 | 45.7145 | #N/A | 45.7209 | 45.7014 | 45.7145 | 45.7145 | 45.6465 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7232 | 45.7232 | 45.7552 | 45.596 | #N/A
Wobbe index - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 45.7145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44.5747 | #N/A | #N/A
Wobbe index - 60% |  |  | 60 | 46.1088 | 45.7344 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 45.7145 | #N/A | #N/A | #N/A | #N/A | #N/A | 43.1595 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 43.5063 | #N/A | #N/A
|  | Efficiency (Hi) | % on Hi
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm
CO emissions - 0% |  | %H2 in test gas | 0 | 226.9343 | 105.409 | 246.4445 | 372.405 | 95 | 61.6507 | 216.9506 | 134.5747 | 594 | 36 | 218 | 122 | #N/A | #N/A | 172.8407 | 10.9937 | 86.1801 | 98.9232 | 568.3506 | 279.611 | 445.5396 | 291.2817 | 82.9168 | 37.4697 | 665.0089 | 239.1779 | #N/A | 86.8073 | 593.276 | 1847.4778 | #N/A
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 891.8075 | #N/A | #N/A
CO emissions - 23% |  |  | 23 | #N/A | #N/A | 194.127 | 561.5816 | 214 | 223.5725 | 173.865 | 252.9484 | 486 | 32 | 393 | 135 | #N/A | #N/A | 158.2796 | 229.8226 | 58.2628 | 76.8698 | 585.275 | 401.642 | 735.7759 | 472.1685 | 86.3292 | 45.6989 | 510.4394 | 70.3319 | #N/A | 112.9073 | #N/A | 1930.3383 | #N/A
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1055.7825 | #N/A | #N/A
CO emissions - 40% |  |  | 40 | #N/A | #N/A | 202.9666 | 642.7275 | 250 | 514.9852 | 182.4236 | 288.4255 | 459 | 68 | 478 | 250 | #N/A | #N/A | 172.5648 | 249.4024 | 69.0111 | 199.8673 | 611.9871 | 609.7349 | 986.2006 | 616.3964 | 79.4622 | 58.9014 | 788.9734 | 51.8086 | #N/A | 165.4749 | 951.2437 | 1921.9712 | #N/A
CO emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 839.5001 | #N/A | #N/A
CO emissions - 60% |  |  | 60 | 188.4087 | 112.6367 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 486.5988 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 802.4258 | #N/A | #N/A
|  | NOx emissions | ppm
NOx emissions - 0% |  | %H2 in test gas | 0 | 66.9165 | 63.2356 | 61.6111 | 46.5506 | #N/A | 68.5275 | 56.6671 | 56.933 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 64.8692 | 3.5103 | 24.6292 | 21.5181 | 36.1985 | 53.7713 | 47.9198 | 19.1935 | 57.6652 | 66.123 | 42.7506 | 30.7661 | #N/A | 28.9436 | 62.257 | 43.6412 | #N/A
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 49.1446 | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | #N/A | #N/A | 54.5982 | 46.7985 | #N/A | 41.6732 | 49.6854 | 45.7249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 60.4919 | 58.8581 | 27.2629 | 18.3497 | 21.5901 | 46.8582 | 41.5986 | 17.0689 | 48.5465 | 55.5603 | 37.0598 | 24.6052 | #N/A | 20.636 | #N/A | 31.1345 | #N/A
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 45.5281 | #N/A | #N/A
NOx emissions - 40% |  |  | 40 | #N/A | #N/A | 47.3589 | 33.8278 | #N/A | 28.3867 | 48.395 | 40.4157 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 50.0731 | 51.7437 | 16.5493 | 7.6945 | 17.9948 | 41.7627 | 34.702 | 16.4147 | 39.0805 | 47.6324 | 29.5007 | 17.2863 | #N/A | 13.8712 | 42.7685 | 33.7188 | #N/A
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 39.4217 | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | 43.6315 | 45.126 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.0296 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 34.8991 | #N/A | #N/A
|  | Qtest (input) | kW
Qtest (input) - 0% |  | %H2 in test gas | 0 | 0.73534 | 0.44436 | #N/A | #N/A | 0.51873 | 0.26155 | 0.58925 | 0.25197 | 0.3584 | 0.28295 | 0.24522 | 0.32067 | #N/A | #N/A | 1.1177 | 1.1113 | 1.0752 | 0.39801 | 1.0664 | 0.476 | 0.26043 | 1.5496 | 0.63719 | 1.2988 | 0.88237 | 0.93372 | #N/A | 0.3814 | 1.0455 | 0.57627 | #N/A
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.87075 | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | 0.22894 | 0.5885 | 0.22211 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.042 | 1.0282 | 0.91022 | 0.37913 | 0.91795 | 0.42993 | 0.22934 | 1.3732 | 0.60497 | 1.171 | 0.91419 | 0.84454 | #N/A | 0.35088 | #N/A | 0.4654 | #N/A
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.85838 | #N/A | #N/A
Qtest (input) - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | 0.44033 | 0.21029 | 0.55725 | 0.2055 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.0146 | 0.97164 | 0.80849 | 0.28603 | 0.78341 | 0.38884 | 0.21199 | 1.3218 | 0.54244 | 1.103 | 0.74474 | 0.80982 | #N/A | 0.33651 | 0.80143 | 0.39908 | #N/A
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.80357 | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | 0.58165 | 0.38417 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.77196 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.79225 | #N/A | #N/A
|  | Flue gases temperatures | [°C]
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | 398 | 104.2 | #N/A | #N/A | #N/A | #N/A | #N/A | 64.63 | 94.87 | #N/A | #N/A | #N/A | #N/A | 77.4 | #N/A | 140 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 260 | #N/A
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | #N/A | #N/A | #N/A | 405 | 97.66 | #N/A | #N/A | #N/A | #N/A | #N/A | 77.16 | 96.44 | #N/A | #N/A | #N/A | #N/A | 90.8 | #N/A | 143.8 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 280 | #N/A
Flue gases temperatures - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 40% |  |  | 40 | #N/A | #N/A | #N/A | 409 | 106.23 | #N/A | #N/A | #N/A | #N/A | #N/A | 79.11 | 88.31 | #N/A | #N/A | #N/A | #N/A | 97.2 | #N/A | 152 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 309 | #N/A
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 156 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO2 emissions | [%]
CO2 emissions - 0% |  | %H2 in test gas | 0 | 1.6 | 1.2775 | 1.7 | 1 | 2.03 | 2.42 | 1.6854 | 1.0101 | 1.4 | 0.91 | 1.18 | 2.33 | #N/A | #N/A | 2.7 | 2.6506 | 3.85 | 1.7099 | 1.72 | 1.515 | 1.02 | 1.6476 | 1.0373 | 2.64 | 0.245 | 2.3539 | #N/A | 1.2401 | 1.3504 | 0.8 | #N/A
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.0984 | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | #N/A | #N/A | 1.8 | 0.7 | 2.17 | 0.94 | 1.61 | 0.95692 | 1.26 | 0.83 | 1.09 | 1.45 | #N/A | #N/A | 2.4 | 2.2611 | 4.07 | 1.8892 | 1.5 | 1.305 | 0.84 | 1.3937 | 0.92887 | 2.27 | 0.25229 | 2.1629 | #N/A | 1.1016 | #N/A | 0.7 | #N/A
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.0437 | #N/A | #N/A
CO2 emissions - 40% |  |  | 40 | #N/A | #N/A | 1.5 | 0.6 | 2.18 | 0.77114 | 1.3179 | 0.73731 | 1.1 | 0.75 | 0.89 | 1.21 | #N/A | #N/A | 2.1291 | 1.9634 | 3.4 | 1.597 | 1.72 | 1.215 | 0.74114 | 1.2192 | 0.8188 | 1.8504 | 0.21547 | 1.8429 | #N/A | 0.94456 | 0.98788 | 0.6 | #N/A
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.91692 | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | 0.9 | 0.56922 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.81773 | #N/A | #N/A
|  | O2 emissions | [%]
O2 emissions - 0% |  | %H2 in test gas | 0 | 18 | 18.6693 | 18.5 | 19.2 | #N/A | 16.95 | 18.0705 | 19.1464 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 16.22 | 16.2599 | 14.54 | 18.9918 | 18.58 | 18.2 | 19.2 | 17.8199 | 18.866 | 16.27 | 20.475 | 16.7213 | #N/A | 18.7205 | 18.6216 | 19.5 | #N/A
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.8244 | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | #N/A | #N/A | 18 | 19.6 | #N/A | 18.91 | 17.76 | 19.1452 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 16.4 | 16.6774 | 14.53 | 18.6958 | 18.85 | 18.495 | 19.35 | 18.2046 | 19.0795 | 16.76 | 20.464 | 16.8379 | #N/A | 18.8028 | #N/A | 19.7 | #N/A
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.8553 | #N/A | #N/A
O2 emissions - 40% |  |  | 40 | #N/A | #N/A | 18.2 | 19.6 | #N/A | 19.467 | 18.2627 | 19.3868 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 16.6742 | 16.971 | 14.65 | 18.5801 | 18.59 | 18.5 | 19.3934 | 18.3473 | 19.2032 | 17.0981 | 20.5129 | 17.2038 | #N/A | 18.8999 | 18.8775 | 19.7 | #N/A
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.9022 | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | 18.8 | 19.5569 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 19.26 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 18.9682 | #N/A | #N/A
|  | Unburnt UHC emissions | ppm
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 90.441 | 100.6898 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 32.1026 | 39.2902 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda)
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 7 | 9.0103 | 8.4 | 11.6667 | #N/A | 5.1852 | 7.1685 | 11.3291 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.3933 | 4.4302 | 3.2508 | 10.4571 | 8.6777 | 7.5 | 11.6667 | 6.6036 | 9.8407 | 4.4397 | 40 | 4.9081 | #N/A | 9.2125 | 8.8294 | 14 | #N/A
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.6525 | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | #N/A | #N/A | 7 | 15 | #N/A | 10.0478 | 6.4815 | 11.3221 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.5652 | 4.8582 | 3.2457 | 9.1138 | 9.7674 | 8.3832 | 12.7273 | 7.5124 | 10.9347 | 4.9528 | 39.1813 | 5.0455 | #N/A | 9.5578 | #N/A | 16.1538 | #N/A
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 9.7917 | #N/A | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | #N/A | #N/A | 7.5 | 15 | #N/A | 13.6983 | 7.6718 | 13.0177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.8546 | 5.2122 | 3.3071 | 8.678 | 8.7137 | 8.4 | 13.0709 | 7.9165 | 11.6876 | 5.3819 | 43.1154 | 5.5319 | #N/A | 9.9995 | 9.8942 | 16.1538 | #N/A
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10.0103 | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | 9.5455 | 14.5518 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 12.069 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10.3355 | #N/A | #N/A
Efficiency, CO & NOx at Qmax
Efficiency, CO & NOx at Qmin

## Seg400a Premix Catering
Do not touch this colum | THyGA Segment 400a - Premix Catering |  |  | THyGA Test data - Values | [9 empty] | Graph for the indicator (KPI): |  |  |  |  | CO emissions
|  |  |  | EB19V02 | EB20V02 | EB03v03 | EB17v01 | GA04 | EB18v01 | EB21V01 | EB22V01 | EB23V01 | EB24V01 |  | EB19V02 | EB20V02 | EB03v03 | EB17v01 | GA04 | EB18v01 | EB21V01 | EB22V01 | EB23V01 | EB24V01
| SEGMENT Nr |  |  | EB19_SEGM_404 | EB19_SEGM_404 | EB03_SEGM_404 | EB17_SEGM_405 | GA4_SEGM_406 | EB18_SEGM_409 | EB21_SEGM_410 | EB22_SEGM_402 | EB23_SEGM_402 | EB24_SEGM_404
|  | Report test lab code |  | 404 | 404 | 404 | 405 | 406 | 409 | 410 | 402 | 402 | 404 | Qmax | Graph title | THyGA Segment 400a - Premix Catering - CO emissions at Qmax | [5 empty] | Y axis | CO emissions (ppm)
|  | Appliance type code (B, CH, CO, F, WH,O) (*) |  | EB19 | EB19 | EB03 | EB17 | GA4 | EB18 | EB21 | EB22 | EB23 | EB24 | %H2 | EB19 | EB20 | EB03 | EB17 | GA04 | EB18 | EB21 | EB22 | EB23 | EB24
|  | Appliance type |  | C (Hot air mode) | C (Damper mode) | Combi-Oven | O | C | O | O | C | C | C | 0 | 3.5073 | 43.0148 | 5.2628 | 102.3289 | 14.0675 | 20.1086 | 93.3917 | 179.6845 | 88.0886 | 39.4507
|  |  |  | 0 | 0 | 0 | 0 | Fryer | 0 | 0 | 0 | 0 | 0 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Burner type |  | 0 | 0 | premix burner | Draught burner | Premix | Multi-ramp tubular slot burner | Tubular or circular burner | Circular burner with holes | Circular burner with holes | multi-ramp tubular slot burner | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | For cooker hobs: burner tested? |  | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 23 | 3.1715 | 25.3979 | 0.78273 | 75.9266 | 8.2382 | 19.5347 | 60.0983 | 137.3309 | 40.6409 | 45.7188
|  | Modulating burner (Y/N) |  | Y | Y | Y* | Y | Y | N | N | Y | Y | N | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Pressure regulator (Y/N) |  | Y | Y | Y (Embedded in the gas valve) | Y | Y | Y | N | N | N | Y | 40 | 4.0021 | 19.5856 | 1.878 | 67.7449 | 7.4144 | 20.8708 | 67.8768 | 23.6891 | 29.9381 | 49.4162
|  | Can the appliance be adjusted (Y/N) |  | Y | Y | N | Y | Y | Y | Y | Y | Y | Y | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Is the appliance equiped with a combustion control (Y/N) |  | Y | Y | N | N | Y | N | N | N | N | N | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | If the appliance can be adjusted. Instructions: |  | 0 | 0 | 0 | CO2 adjustments | ask Eric if it is a CO2 adjustment | nozzle / nozzle pressure | nozzle / nozzle pressure | Nozzle/Nozzle pressure | Nozzle/Nozzle pressure | Nozzle/Nozzle Pressure
|  | If Yes what technology is used? |  | Pneumatic Air-Gas Ratio System | Pneumatic Air-Gas Ratio System | 0 | 0 | Ionisation | 0 | 0 | 0 | 0 | 0
|  | Max. power input (net) [kW] |  | 13 | 13 | 19 | 20 | 31 | 10.6 | 20 | 7 | 3.5 | 6 | Qmin | Graph title | THyGA Segment 400a - Premix Catering - CO emissions at Qmin | [5 empty] | Y axis | CO emissions (ppm)
|  | Min. power input (net) [kW] |  | 5 | 5 | NA | 3 | 16 | - | 12 | 2 | 1 | - | %H2 | EB19 | EB20 | EB03 | EB17 | GA04 | EB18 | EB21 | EB22 | EB23 | EB24
|  | Flue type |  | A3/B23 | A3/B23 | A3 | A3 | A3 | NA (A1) | NA (A1) | A1 | A1 | A1 | 0 | 10.1475 | 14.8601 | 3.1012 | 24.0031 | 7.7931 | #N/A | 80.9535 | 54.0014 | 538.259 | #N/A
|  | Flue lenght |  | NR | NR | NA | NR | NA | NA | NA | NA | NA | - | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Applicable standard(s) |  | EN 203 | EN 203 | EN 203-2-2 | EN203 | EN203-1 and EN203-4 | EN 203 | EN 203 | EN 203 | EN 203 | EN 203 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Gas category |  | II2R3R | II2R3R | G 20, G25/G25.1, G30 & G31 | II2ELL3B/P | I2E( R ) | II2ELL3B/P | II2ELL3B/P | II2ELL3B/P | II2ELL3B/P | II2ELL3B/P | 23 | 18.8596 | 13.1736 | 3.1471 | 28.54 | 5.7225 | #N/A | 82.049 | 102.2074 | 360.8516 | #N/A
|  | Origin of the appliance |  | Germany | Germany | Italy | Germany | New device, but already used for another project (3 test days). | Germany | Germany | Germany | Germany | Germany | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Manufacture year |  | 2022 | 2022 | 2019 | 2022 | 2019 | 2022 | 2019 | 2022 | 2022 | 2022 | 40 | 9.8603 | 13.3983 | 0.78412 | 35.7162 | 4.5689 | #N/A | 96.3214 | 109.8074 | 255.4858 | #N/A
[5 empty] | EB20 | [8 empty] | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[14 empty] | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
QMAX
H2
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 23% |  |  | 23 | 23 | 23 | 23.2 | 23 | 23.0513 | 23 | 23 | 23 | 23 | 23
H2 - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 40% |  |  | 40 | 40 | 40 | 39.4 | 40 | 40 | 40 | 40 | 40 | 40 | 40
H2 - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 53.4706 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063
Wobbe index - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | 47.7776 | 47.7776 | 47.753 | 47.7776 | 50.2872 | 47.7776 | 47.7776 | 47.7776 | 47.7776 | 47.7776
Wobbe index - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 40% |  |  | 40 | 45.7145 | 45.7145 | 45.7858 | 45.7145 | 48.0676 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7145
Wobbe index - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 3.5073 | 43.0148 | 5.2628 | 102.3289 | 14.0675 | 20.1086 | 93.3917 | 179.6845 | 88.0886 | 39.4507
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | 3.1715 | 25.3979 | 0.78273 | 75.9266 | 8.2382 | 19.5347 | 60.0983 | 137.3309 | 40.6409 | 45.7188
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 40% |  |  | 40 | 4.0021 | 19.5856 | 1.878 | 67.7449 | 7.4144 | 20.8708 | 67.8768 | 23.6891 | 29.9381 | 49.4162
CO emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | 36.3095 | 31.2806 | 24.1503 | #N/A | 43.4813 | 63.3385 | 112.0701 | 84.1333 | 70.0798 | 96.7334
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | 21.7926 | 17.9364 | 17.4721 | #N/A | 21.5842 | 60.8966 | 73.5603 | 83.4907 | 65.3605 | 90.1773
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 40% |  |  | 40 | 13.3645 | 10.5057 | 15.0446 | #N/A | 13.6424 | 54.474 | 72.2403 | 95.7025 | 53.5139 | 73.2491
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 12.9249 | 12.6175 | 23.9648 | 19.3974 | 32.1869 | 10.237 | 17.1847 | 7.2929 | 3.9698 | 6.4174
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | 12.5492 | 11.5273 | 22.5859 | 18.4677 | 29.4686 | 9.6135 | 16.4232 | 6.7966 | 3.3315 | 5.7195
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 40% |  |  | 40 | 12.0859 | 10.7937 | 17.7976 | 17.3608 | 27.7357 | 9.0911 | 15.7044 | 6.135 | 3.1607 | 5.275
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 478.4092 | 190.6028 | 183.295 | 281.7164 | 166.6 | 384.1587 | #N/A | 161.3956 | 124.8108 | 63.9911
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | 460.6473 | 185.6643 | 187.9738 | 269.2494 | 147 | 368.497 | #N/A | 185.1375 | 133.7656 | 102.9477
Flue gases temperatures - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 40% |  |  | 40 | 450.7067 | 185.8002 | 181.0585 | 263.4474 | 145.6 | 359.8229 | #N/A | 179.6684 | 116.3324 | 121.8991
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 9.3501 | 9.366 | 7.6499 | 9.162 | 9.1 | 6.4691 | 3.14 | 7.6413 | 5.0283 | 3.5122
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | 8.0995 | 8.0328 | 5.9836 | 7.8767 | 7.95 | 5.4151 | 2.29 | 7.2276 | 4.0355 | 2.6875
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 40% |  |  | 40 | 6.9636 | 6.9616 | 5.6562 | 6.7443 | 6.84 | 4.6906 | 2.11 | 5.2197 | 3.8198 | 2.2418
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | 5.08 | 4.2897 | 7.121 | #N/A | #N/A | 9.4093 | 15.3785 | 7.1706 | 12.0573 | 14.3986
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | 6.5623 | 5.5719 | 8.8949 | #N/A | #N/A | 10.1333 | 17.2 | 7.5682 | 13.5627 | 15.5523
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 40% |  |  | 40 | 7.6662 | 6.5456 | 8.9065 | #N/A | #N/A | 10.775 | 16.76 | 9.6843 | 13.8907 | 16.1438
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | 1011.3348 | 1644.1887 | #N/A | 1867.4006 | 434.1945 | 2225.2865 | 13786.9948 | 907.703 | 283.9391 | 3164.8627
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | 1860.5701 | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | 246.9665 | 916.2092 | #N/A | 1228.8301 | 253.2412 | 1198.3023 | 6682.4854 | 162.7674 | 356.8895 | 1759.9247
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 1.3191 | 1.2567 | 1.5131 | #N/A | #N/A | 1.8118 | 3.7357 | 1.5185 | 2.3483 | 3.1811
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | 1.4545 | 1.3612 | 1.7348 | #N/A | #N/A | 1.9325 | 5.5263 | 1.5635 | 2.8236 | 3.8548
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | 1.5749 | 1.4528 | 1.7365 | #N/A | #N/A | 2.0538 | 4.9528 | 1.8558 | 2.9539 | 4.3244
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qmin
|  | H2 | %
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A
H2 - 23% |  |  | 23 | 23 | 23 | 23.2 | 23 | 23.0513 | 40 | 23 | 23 | 23 | 23
H2 - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A
H2 - 40% |  |  | 40 | 40 | 40 | 39.4 | 40 | 40 | 40 | 40 | 40 | 40 | 40
H2 - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A
H2 - 60% |  |  | 60 | #N/A | 40 | #N/A | #N/A | #N/A | 40 | #N/A | #N/A | #N/A | #N/A
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 45.7145 | 50.6063 | 50.6063 | 50.6063 | 50.6063
Wobbe index - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | 45.7145 | #N/A | #N/A | #N/A | #N/A
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | 45.7145 | #N/A | #N/A | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | 47.7776 | 47.7776 | 47.753 | 47.7776 | 47.5934 | 45.7145 | 47.7776 | 47.7776 | 47.7776 | 47.7776
Wobbe index - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | 45.7145 | #N/A | #N/A | #N/A | #N/A
Wobbe index - 40% |  |  | 40 | 45.7145 | 45.7145 | 45.7858 | 45.7145 | 45.4927 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7145
Wobbe index - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 45.7145 | #N/A | #N/A | #N/A | #N/A
Wobbe index - 60% |  |  | 60 | #N/A | 45.7145 | #N/A | #N/A | #N/A | 45.7145 | #N/A | #N/A | #N/A | #N/A
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 10.1475 | 14.8601 | 3.1012 | 24.0031 | 7.7931 | #N/A | 80.9535 | 54.0014 | 538.259 | #N/A
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | 18.8596 | 13.1736 | 3.1471 | 28.54 | 5.7225 | #N/A | 82.049 | 102.2074 | 360.8516 | #N/A
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 40% |  |  | 40 | 9.8603 | 13.3983 | 0.78412 | 35.7162 | 4.5689 | #N/A | 96.3214 | 109.8074 | 255.4858 | #N/A
CO emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | 16.2465 | 16.0688 | 50.5091 | #N/A | 42.8619 | #N/A | 57.8239 | 72.6589 | 45.4463 | #N/A
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | 7.7675 | 8.8532 | 42.8655 | #N/A | 19.8285 | #N/A | 56.8032 | 64.9475 | 45.6153 | #N/A
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 40% |  |  | 40 | 6.4995 | 5.3137 | 25.5814 | #N/A | 11.5744 | #N/A | 43.8429 | 58.8143 | 38.0653 | #N/A
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 5.3411 | 5.4901 | 5.9508 | 2.8959 | 16.3967 | #N/A | 11.1078 | 1.8506 | 0.8656 | #N/A
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | 5.2777 | 4.8614 | 5.6589 | 2.7934 | 15.0035 | #N/A | 10.5922 | 1.6783 | 0.76816 | #N/A
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 40% |  |  | 40 | 5.0058 | 4.6627 | 5.5083 | 2.6226 | 14.1578 | #N/A | 10.1036 | 1.5696 | 0.70954 | #N/A
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 157.3159 | 133.6598 | 146.1927 | 100.4546 | 104 | #N/A | #N/A | 136.9873 | 98.0375 | #N/A
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | 154.025 | 132.9834 | 161.0881 | 92.7048 | 104.4 | #N/A | #N/A | 126.925 | 92.8302 | #N/A
Flue gases temperatures - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 40% |  |  | 40 | 150.7922 | 131.8941 | 160.1533 | 91.7664 | 99.3 | #N/A | #N/A | 124.6394 | 91.363 | #N/A
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 8.7092 | 8.8383 | 7.3369 | 7.0465 | 8.96 | #N/A | 1.42 | 2.9098 | 2.5971 | #N/A
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | 7.2835 | 7.6697 | 7.0563 | 6.0824 | 7.63 | #N/A | 1.57 | 2.7223 | 2.4301 | #N/A
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 40% |  |  | 40 | 6.5198 | 6.649 | 5.8403 | 5.238 | 6.66 | #N/A | 1.54 | 2.2757 | 2.4265 | #N/A
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | 6.0249 | 5.0256 | 7.4566 | #N/A | #N/A | #N/A | 18.81 | 15.6504 | 16.1286 | #N/A
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | 7.5332 | 6.179 | 7.2542 | #N/A | #N/A | #N/A | 18.23 | 16.2415 | 16.3595 | #N/A
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 40% |  |  | 40 | 7.8851 | 7.1207 | 8.4129 | #N/A | #N/A | #N/A | 18.27 | 16.456 | 16.7766 | #N/A
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | 446.8984 | 753.5568 | #N/A | 1494.1172 | #N/A | #N/A | 8347.5856 | 90.5842 | 241.2545 | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | 72.0522 | 280.1677 | #N/A | 530.7691 | #N/A | #N/A | 4929.9108 | 31.4595 | 111.4655 | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 1.4023 | 1.3146 | 1.5506 | #N/A | #N/A | #N/A | 9.589 | 3.9255 | 4.3109 | #N/A
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | 1.5594 | 1.4169 | 1.5277 | #N/A | #N/A | #N/A | 7.5812 | 4.4132 | 4.5254 | #N/A
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | 1.6012 | 1.513 | 1.6684 | #N/A | #N/A | #N/A | 7.6923 | 4.6215 | 4.9723 | #N/A
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## Seg400b Non Premix Catering
Do not touch this colum | THyGA Segment 400b - Non Premix Catering |  |  | THyGA Test data - Values | [5 empty] | Graph for the indicator (KPI): |  |  |  |  | NOx emissions
|  |  |  | EB14v01 | EB04v04 | EB05v04 | EB06v03 | GA03 | GA17v03 |  | EB14v01 | EB04v04 | EB05v04 | EB06v03 | GA03 | GA17v03
| SEGMENT Nr |  |  | EB14_SEGM_401 | EB04_SEGM_402 | EB05_SEGM_402 | EB06_SEGM_408 | GA3_SEGM_407 | GA_17_SEGM_406
|  | Report test lab code |  | 401 | 402 | 402 | 408 | 407 | 406 | Qmax | Graph title | THyGA Segment 400b - Non Premix Catering - NOx emissions at Qmax |  |  |  |  | Y axis | NOx emissions (ppm)
|  | Appliance type code (B, CH, CO, F, WH,O) (*) |  | EB14 | EB04 | EB05 | EB06 | GA3 | GA_17 | %H2 | EB14 | EB04 | EB05 | EB06 | GA03 | GA17
|  | Appliance type |  | C | Catering | Catering - Cooker Hobs | O - Braising pan (Brat pan) | C | O | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | 75.2785
|  |  |  | 0 | 0 | 0 | 0 | Catering (O) | 0 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Burner type |  | Wok Burner 12 kW | Venturi + 6kW atmospheric open burner | Venturi + 10kW atmospheric open burner | 0 | Atmospheric | atmospheric | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | For cooker hobs: burner tested? |  | 0 | 0 | 0 | atmospheric burner | NA | na | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | 63.0816
|  | Modulating burner (Y/N) |  | N | N | N | N | N | no | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Pressure regulator (Y/N) |  | N | N | N | Y - embedded in the gas valve (excluded) | N | yes | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Can the appliance be adjusted (Y/N) |  | N | N | N | N | N | no | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Is the appliance equiped with a combustion control (Y/N) |  | N | N | N | N | N | no | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | If the appliance can be adjusted. Instructions: |  | 0 | 0 | 0 | 0 | N | na
|  | If Yes what technology is used? |  | 0 | 0 | 0 | 0 | N | na
|  | Max. power input (net) [kW] |  | 12 | 6 | 10 | 21 | 5.9 | 15 | Qmin | Graph title | THyGA Segment 400b - Non Premix Catering - NOx emissions at Qmin |  |  |  |  | Y axis | NOx emissions (ppm)
|  | Min. power input (net) [kW] |  | 4.15 | 1.55 | 2.5 | NA | Not specified | na | %H2 | EB14 | EB04 | EB05 | EB06 | GA03 | GA17
|  | Flue type |  | A1 | NR | NR | A1 | A1 | B22 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Flue lenght |  | NR | NR | NR | NA | na | min | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Applicable standard(s) |  | EN 203-2-1 | EN 203-2-1 | EN 203-2-1 | EN 203-1, EN 203-2-8 | EN 203-1 and EN 203-2-7 | EN203-1 AND EN 203-4 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Gas category |  | II2H3B/P | II2ELL3B/P at 20 & 50 mbar | II2ELL3B/P at 20 & 50 mbar | II2ELL3B/P | II2E+3+ | I2E+ | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Origin of the appliance |  | Switzerland | Italy | Italy | Italy | New appliance, it was a back-up appliance for another project. | Already used for other project | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Manufacture year |  | 2022 | 2021 | 2021 | 2021 | Not specified | 2019 | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[10 empty] | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[10 empty] | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
QMAX
H2
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | #N/A | #N/A | 10.5 | #N/A | #N/A
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | 20.4 | #N/A | #N/A
H2 - 23% |  |  | 23 | 22.1 | 23 | 23 | 23.4 | 23 | 23
H2 - 30% |  |  | 30 | #N/A | #N/A | #N/A | 30.2 | #N/A | 30
H2 - 40% |  |  | 40 | 39.4 | 40 | 40 | 39.8 | 40 | 40
H2 - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 53.4706 | 50.6063
Wobbe index - 10% |  |  | 10 | #N/A | #N/A | #N/A | 49.3171 | #N/A | 50.6063
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | 48.0975 | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | 47.8883 | 47.7776 | 47.7776 | 47.7284 | 50.4818 | 47.7776
Wobbe index - 30% |  |  | 30 | #N/A | #N/A | #N/A | 46.8956 | #N/A | 46.92
Wobbe index - 40% |  |  | 40 | 45.7858 | 45.7145 | 45.7145 | 45.7382 | 48.3019 | 45.7145
Wobbe index - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | #N/A | 53.55 | 52.96 | #N/A | #N/A | 53.44
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | 53.45 | 50.41 | #N/A | #N/A | 59.37
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 40% |  |  | 40 | #N/A | 55.55 | 52.88 | #N/A | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 481.3845 | 427.3118 | 724.0232 | 387.3009 | 2001.1365 | 22.1767
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 321.5367 | #N/A | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 178.0024 | #N/A | #N/A
CO emissions - 23% |  |  | 23 | 127.8868 | 230.0581 | 326.6847 | 148.8598 | 885.1164 | 17.6193
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | 131.4843 | #N/A | #N/A
CO emissions - 40% |  |  | 40 | 27.4828 | 167.7529 | 184.2548 | 106.1013 | 224.5566 | #N/A
CO emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | 75.2785
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | 63.0816
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 10.443 | 6.2494 | 10.86 | 17.2357 | 6.1985 | 16.8946
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | 16.7251 | #N/A | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | 16.5243 | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | 9.6845 | 5.8588 | 10.0694 | 16.0887 | 5.9616 | 14.4448
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | 15.7411 | #N/A | #N/A
Qtest (input) - 40% |  |  | 40 | 9.1122 | 5.4884 | 9.4664 | 15.3201 | 5.5903 | #N/A
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | 315
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | 298
Flue gases temperatures - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 5.9372 | 3.3836 | 5.785 | 2.5531 | 0.517 | 5.72
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | 1.9242 | #N/A | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 2.1277 | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | 4.9581 | 2.1557 | 4.7806 | 2.0944 | 0.454 | 5.02
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | 1.8123 | #N/A | #N/A
CO2 emissions - 40% |  |  | 40 | 4.1729 | 0.67261 | 4.0125 | 1.7516 | 0.408 | #N/A
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | 20.017 | #N/A
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | 20.03 | #N/A
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | 20.1 | #N/A
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | 1031.2823 | #N/A | #N/A | 8352.6185 | 159.9123 | 179.8921
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | 168.0587
Unburnt UHC emissions - 40% |  |  | 40 | 1640.2563 | #N/A | #N/A | 5265.9795 | 150.2993 | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | 21.3632 | #N/A
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | 21.6495 | #N/A
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | 23.3333 | #N/A
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qmin
|  | H2 | %
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | 40 | #N/A | 40
H2 - 10% |  |  | 10 | #N/A | #N/A | #N/A | 40 | #N/A | 40
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | 40 | #N/A | 40
H2 - 23% |  |  | 23 | 24.4 | 23 | 23 | 40 | 23 | 40
H2 - 30% |  |  | 30 | #N/A | #N/A | #N/A | 40 | #N/A | 40
H2 - 40% |  |  | 40 | 40.6 | 40 | 40 | 40 | 40 | 40
H2 - 50% |  |  | 50 | #N/A | #N/A | #N/A | 40 | #N/A | 40
H2 - 60% |  |  | 60 | #N/A | #N/A | #N/A | 40 | #N/A | 40
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6063 | 50.6063 | 50.6063 | 45.7145 | 50.6063 | 45.7145
Wobbe index - 10% |  |  | 10 | #N/A | #N/A | #N/A | 45.7145 | #N/A | 45.7145
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | 45.7145 | #N/A | 45.7145
Wobbe index - 23% |  |  | 23 | 47.6056 | 47.7776 | 47.7776 | 45.7145 | 47.7776 | 45.7145
Wobbe index - 30% |  |  | 30 | #N/A | #N/A | #N/A | 45.7145 | #N/A | 45.7145
Wobbe index - 40% |  |  | 40 | 45.6433 | 45.7145 | 45.7145 | 45.7145 | 45.7145 | 45.7145
Wobbe index - 50% |  |  | 50 | #N/A | #N/A | #N/A | 45.7145 | #N/A | 45.7145
Wobbe index - 60% |  |  | 60 | #N/A | #N/A | #N/A | 45.7145 | #N/A | 45.7145
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 528.9245 | 136.1076 | 720.8379 | #N/A | 843.2312 | #N/A
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | 178.9704 | 98.6638 | 175.652 | #N/A | 913.9638 | #N/A
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 40% |  |  | 40 | 134.7932 | 86.6511 | 95.3183 | #N/A | 960.6157 | #N/A
CO emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 1.7487 | 1.2335 | 2.0401 | #N/A | 3.6682 | #N/A
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | 1.592 | 1.1619 | 1.9227 | #N/A | 3.1575 | #N/A
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 40% |  |  | 40 | 1.5089 | 1.0851 | 1.8137 | #N/A | 3.0636 | #N/A
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 2.9145 | 1.4972 | 1.9847 | #N/A | 0.35 | #N/A
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | 2.6431 | 1.5162 | 1.6544 | #N/A | 0.319 | #N/A
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 40% |  |  | 40 | 2.3654 | 1.3666 | 1.5273 | #N/A | 0.292 | #N/A
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## Seg500 Space Heaters
Do not touch this colum | THyGA Segment 500 - Space Heaters |  |  | THyGA Test data - Values |  |  |  | Graph for the indicator (KPI): |  |  |  |  | CO emissions
|  |  |  | GA02 | GA06V03 | GA07v03 | GA08v02 |  | GA02 | GA06V03 | GA07v03 | GA08v02
| SEGMENT Nr |  |  | GA2_SEGM_503 | GA6_SEGM_507 | GA7_SEGM_503 | GA8_SEGM_504
|  | Report test lab code |  | 503 | 502 | 502 | 504 | Qmax | Graph title | THyGA Segment 500 - Space Heaters - CO emissions at Qmax |  |  |  | Y axis | CO emissions (ppm)
|  | Appliance type code (B, CH, CO, F, WH,O) (*) |  | GA2 | GA6 | GA7 | GA8 | %H2 | GA02 | GA06 | GA07 | GA08
|  | Appliance type |  | EN613 Convection heater | F | Fires | F | 0 | 168.8291 | 2.1712 | 306.9977 | 376.9175
|  |  |  | F |  |  |  | 10 | #N/A | #N/A | #N/A | #N/A
|  | Burner type |  | Atmospheric | atmospheric | atmospheric | Atmosperhic | 20 | #N/A | #N/A | #N/A | #N/A
|  | For cooker hobs: burner tested? |  | NA | NA | NA | na | 23 | 167.0063 | #N/A | 301.8826 | 350.688
|  | Modulating burner (Y/N) |  | Y | Y | Y | Y | 30 | #N/A | #N/A | #N/A | #N/A
|  | Pressure regulator (Y/N) |  | Y | N | Y ( only for min.heat input) | Y | 40 | 157.2291 | 2.5627 | 294.27 | 327.3654
|  | Can the appliance be adjusted (Y/N) |  | N | N | NO | N | 50 | 157.6071 | #N/A | #N/A | #N/A
|  | Is the appliance equiped with a combustion control (Y/N) |  |  | N | NA | N | 60 | 153.6951 | #N/A | #N/A | #N/A
|  | If the appliance can be adjusted. Instructions: |  | N | N | NA | na
|  | If Yes what technology is used? |  | NA | NA | NA | na
|  | Max. power input (net) [kW] |  | 5.8 | 5.36 | 10.2 | 10 | Qmin | Graph title | THyGA Segment 500 - Space Heaters - CO emissions at Qmin |  |  |  | Y axis | CO emissions (ppm)
|  | Min. power input (net) [kW] |  | 3.1 | NA | Not specified | 3.3 | %H2 | GA02 | GA06 | GA07 | GA08
|  | Flue type |  | C11 | B11BS | C11 | BAs | 0 | #N/A | 29.4687 | 1132.9032 | 1237.1121
|  | Flue lenght |  | 1m + elbow 90°+terminal | 1m | 1mVertical+ elbow90°+ Terminal | na | 10 | #N/A | #N/A | #N/A | #N/A
|  | Applicable standard(s) |  | EN 613 | EN613 | EN613 | EN 13278 | 20 | #N/A | #N/A | #N/A | #N/A
|  | Gas category |  | I2E+ | I2E+ | I2E+ | I2E+ | 23 | #N/A | #N/A | 1166.7981 | 1813.4562
|  | Origin of the appliance |  | Already used for other project . Received september 2016 . | Already used for another project | New appliance | new appliance | 30 | #N/A | #N/A | #N/A | #N/A
|  | Manufacture year |  | 2016 | 2013 | 2020 | 2021 | 40 | #N/A | 30.7525 | 961.2325 | 1885.5133
[8 empty] | 50 | #N/A | #N/A | #N/A | #N/A
[8 empty] | 60 | #N/A | #N/A | #N/A | #N/A
QMAX
H2
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
H2 - 23% |  |  | 23 | 23 | #N/A | 23 | 22.8
H2 - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
H2 - 40% |  |  | 40 | 40 | 40 | 40 | 40
H2 - 50% |  |  | 50 | 50 | #N/A | #N/A | #N/A
H2 - 60% |  |  | 60 | 60 | #N/A | #N/A | #N/A
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6604 | #N/A | 50.6063 | 53.4706
Wobbe index - 10% |  |  | 10 | #N/A | 50.6063 | #N/A | #N/A
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | 47.8168 | #N/A | 47.7776 | 50.5078
Wobbe index - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
Wobbe index - 40% |  |  | 40 | 45.7405 | 45.7145 | 45.7145 | 48.3019
Wobbe index - 50% |  |  | 50 | 44.57 | #N/A | #N/A | #N/A
Wobbe index - 60% |  |  | 60 | 43.5063 | #N/A | #N/A | #N/A
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 79.52 | #N/A | #N/A | #N/A
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 20% |  |  | 20 | 80.04 | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | 80.32 | #N/A | #N/A | #N/A
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | 79.2 | #N/A | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 168.8291 | 2.1712 | 306.9977 | 376.9175
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | 167.0063 | #N/A | 301.8826 | 350.688
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
CO emissions - 40% |  |  | 40 | 157.2291 | 2.5627 | 294.27 | 327.3654
CO emissions - 50% |  |  | 50 | 157.6071 | #N/A | #N/A | #N/A
CO emissions - 60% |  |  | 60 | 153.6951 | #N/A | #N/A | #N/A
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | 58.7425 | 117.245 | 74.8098 | 118.7516
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | 64.8755 | #N/A | 75.0725 | 76.2365
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
NOx emissions - 40% |  |  | 40 | 66.1391 | 109.684 | 76.9004 | 54.5609
NOx emissions - 50% |  |  | 50 | 57.0387 | #N/A | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | 47.2908 | #N/A | #N/A | #N/A
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 6.3897 | 5.4555 | 10.1972 | 10.1864
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | 5.9417 | #N/A | 9.5076 | 9.1054
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 40% |  |  | 40 | 5.2922 | 4.955 | 8.9618 | 8.7826
Qtest (input) - 50% |  |  | 50 | 5.3384 | #N/A | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | 5.4685 | #N/A | #N/A | #N/A
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 219.83 | 188 | 275.41 | #N/A
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | 265 | #N/A
Flue gases temperatures - 23% |  |  | 23 | 210.11 | #N/A | 265 | #N/A
Flue gases temperatures - 30% |  |  | 30 | #N/A | 189 | 258.6 | #N/A
Flue gases temperatures - 40% |  |  | 40 | 205.83 | 189 | 258.6 | #N/A
Flue gases temperatures - 50% |  |  | 50 | 201 | #N/A | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | 201.36 | #N/A | #N/A | #N/A
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 4.2 | 5.36 | 4.53 | 0.49
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | 3.4 | #N/A | 3.84 | 0.43
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 40% |  |  | 40 | 2.9 | 3.96 | 3.22 | 0.372
CO2 emissions - 50% |  |  | 50 | 2.55 | #N/A | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | 2.22 | #N/A | #N/A | #N/A
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | 13.4 | 13.12 | 14 | #N/A
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | 14.4 | #N/A | 14.64 | #N/A
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
O2 emissions - 40% |  |  | 40 | 14.94 | 14.4 | 15.15 | #N/A
O2 emissions - 50% |  |  | 50 | 15.22 | #N/A | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | 15.66 | #N/A | #N/A | #N/A
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | 53.1619 | 734.7268 | 760.6276
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | 32.5652 | #N/A | 351.6359
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | 469.8899 | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | 153 | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 2.7632 | 2.665 | 2.5778 | #N/A
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | 3.1818 | #N/A | 2.8736 | #N/A
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | 3.4653 | 3.1818 | 3.1712 | #N/A
Air Excess (Lambda) - 50% |  |  | 50 | 3.6332 | #N/A | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | 3.9326 | #N/A | #N/A | #N/A
Qmin
|  | H2 | % | #N/A | #N/A | #N/A | #N/A
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
H2 - 23% |  |  | 23 | #N/A | #N/A | 23 | 22.8
H2 - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
H2 - 40% |  |  | 40 | #N/A | 40 | 40 | 40
H2 - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A
H2 - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | #N/A | 50.6063 | 50.6063 | 50.6063
Wobbe index - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | #N/A | #N/A | 47.7776 | 47.8022
Wobbe index - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
Wobbe index - 40% |  |  | 40 | #N/A | 45.7145 | 45.7145 | 45.7145
Wobbe index - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A
Wobbe index - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | #N/A | 29.4687 | 1132.9032 | 1237.1121
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | #N/A | #N/A | 1166.7981 | 1813.4562
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
CO emissions - 40% |  |  | 40 | #N/A | 30.7525 | 961.2325 | 1885.5133
CO emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | #N/A | 66.4295 | 50.1512 | 156.4727
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | #N/A | #N/A | 59.5617 | 104.6225
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
NOx emissions - 40% |  |  | 40 | #N/A | 51.0492 | 45.7389 | 57.661
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | #N/A | 2.3221 | 4.2428 | 3.3203
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | #N/A | #N/A | 4.2135 | 3.0507
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 40% |  |  | 40 | #N/A | 2.1115 | 4.2351 | 2.9501
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | #N/A | 134 | 172.86 | #N/A
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | #N/A | #N/A | 163.65 | #N/A
Flue gases temperatures - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 40% |  |  | 40 | #N/A | 126 | 162.6 | #N/A
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | 2.33 | 1.81 | 0.238
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | #N/A | #N/A | 1.43 | 0.188
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 40% |  |  | 40 | #N/A | 1.65 | 1.42 | 0.176
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | 17.55 | 18.15 | #N/A
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | #N/A | #N/A | 18.4 | #N/A
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
O2 emissions - 40% |  |  | 40 | #N/A | 17.9 | 18.33 | #N/A
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | #N/A | 6.087 | 7.3684 | #N/A
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | #N/A | #N/A | 8.0769 | #N/A
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | #N/A | 6.7742 | 7.8652 | #N/A
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A

## Seg600 C-H-P
Do not touch this colum | THyGA Segment 600 - C-H-P |  |  | THyGA Test data - Values |  |  |  |  | Graph for the indicator (KPI): |  |  |  |  | CO2 emissions
|  |  |  | GA12V03 | GA13V01 | GW09V03 | EN20V01 | D11 |  | GA12V03 | GA13V01 | GW09V03 | EN20V01 | D11
| SEGMENT Nr |  |  | GA12_SEGM_604 | GA13_SEGM_605 | GW09_SEGM_602 |  | 0
|  | Report test lab code |  | 604 | 605 | 602 | 60 | 12 | Qmax | Graph title | THyGA Segment 600 - C-H-P - CO2 emissions at Qmax |  |  |  | Y axis | CO2 emissions (%)
|  | Appliance type code (B, CH, CO, F, WH,O) (*) |  | GA12 | GA13 | GW09 | EN20 | D11 | %H2 | GA12 | GA13 | GW09 | EN20 | D11
|  | Appliance type |  | O | O | CHP | CH | EN 50465 Internal Combustion Engine | 0 | 0.5 | 2.7 | 6.34 | 1.45 | 7.6761
|  |  |  | PEM Fuel cell |  |  |  |  | 10 | 0.5 | 2.6 | 6.14 | 1.46 | #N/A
|  | Burner type |  | premix | unknow | / | Heating & Electricity | NA | 20 | 0.5 | 2.5 | #N/A | #N/A | #N/A
|  | For cooker hobs: burner tested? |  | NA | NA |  |  | NA | 23 | 0.45 | 2.5 | 5.71 | 1.33 | 6.6486
|  | Modulating burner (Y/N) |  | NA | N | Y | Y | NA | 30 | #N/A | 2.4 | 5.46 | 1.3 | #N/A
|  | Pressure regulator (Y/N) |  | NA | N | Y |  | Y | 40 | #N/A | #N/A | 5.11 | #N/A | 5.8582
|  | Can the appliance be adjusted (Y/N) |  | NA | N | N | N | Y | 50 | #N/A | #N/A | 4.76 | #N/A | #N/A
|  | Is the appliance equiped with a combustion control (Y/N) |  | NO | N | N | Y | Y (see comment) | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | If the appliance can be adjusted. Instructions: |  | NA | N |  | N | NA
|  | If Yes what technology is used? |  | NA | N |  |  | na
|  | Max. power input (net) [kW] |  | 2 | 3.2 | 19.5 | 20 | 49.6 (100 % Power Modulation) | Qmin | Graph title | THyGA Segment 600 - C-H-P - CO2 emissions at Qmin |  |  |  | Y axis | CO2 emissions (%)
|  | Min. power input (net) [kW] |  | NA | 1.1 | 9.7 | 9.4 | 30.5 (50 % Power Modulation) | %H2 | GA12 | GA13 | GW09 | EN20 | D11
|  | Flue type |  | C33 | B33 |  | B23, C53, C63 | 60 mm PP duct | 0 | #N/A | #N/A | 6.63 | 0.75 | 7.9439
|  | Flue lenght |  | MIN | 1 | 3m | 1.5 M | 1.8 m | 10 | #N/A | #N/A | 6.33 | 0.78 | #N/A
|  | Applicable standard(s) |  | EN 50465 | EN 50465 |  |  | EN 50465 | 20 | #N/A | #N/A | #N/A | 0.7 | #N/A
|  | Gas category |  | I2E(S) | I2N | II2ELL3P | I2E(S) BE | II 2H3B/P | 23 | #N/A | #N/A | 5.85 | #N/A | 6.7761
|  | Origin of the appliance |  | NEW | NEW | GWI own from another project | University Mons Belgium | Manufacturer | 30 | #N/A | #N/A | 5.62 | #N/A | #N/A
|  | Manufacture year |  | 2022 | 2021 |  | 2020 | 2019 | 40 | #N/A | #N/A | 5.27 | #N/A | 5.8473
[9 empty] | 50 | #N/A | #N/A | 4.9 | #N/A | #N/A
[9 empty] | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
QMAX
H2
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | 10.1 | 10.7 | 10 | 10.11 | #N/A
H2 - 20% |  |  | 20 | 19.7 | 21.7 | #N/A | #N/A | #N/A
H2 - 23% |  |  | 23 | 24.9 | 22.9 | 23 | 23.07 | 21.0715
H2 - 30% |  |  | 30 | 30 | 31.3 | 30 | 23.07 | #N/A
H2 - 40% |  |  | 40 | #N/A | 40 | 40 | #N/A | 37.6824
H2 - 50% |  |  | 50 | #N/A | #N/A | 50 | #N/A | #N/A
H2 - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063
Wobbe index - 10% |  |  | 10 | 49.3664 | 49.2925 | 49.354 | 49.3651 | #N/A
Wobbe index - 20% |  |  | 20 | 48.1837 | 47.9641 | #N/A | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | 47.5442 | 47.7899 | 47.7899 | 47.769 | 48.0148
Wobbe index - 30% |  |  | 30 | 46.92 | 46.7616 | 46.92 | 47.769 | #N/A
Wobbe index - 40% |  |  | 40 | #N/A | 45.7145 | 45.7263 | #N/A | 45.9908
Wobbe index - 50% |  |  | 50 | #N/A | #N/A | 44.5802 | #N/A | #N/A
Wobbe index - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 53.901 | 29.1315 | 73 | 81.6945 | #N/A
Efficiency (Hi) - 10% |  |  | 10 | 55.7175 | 28.513 | 74.5 | 82.0837 | #N/A
Efficiency (Hi) - 20% |  |  | 20 | 57.8959 | 26.6825 | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | 55.3503 | 27.2866 | 74.69 | 81.5198 | #N/A
Efficiency (Hi) - 30% |  |  | 30 | #N/A | 28.7825 | 72 | 82.4586 | #N/A
Efficiency (Hi) - 40% |  |  | 40 | #N/A | #N/A | 72.3 | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | 74 | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 13.9652 | 185.7715 | 10.7 | 154.8209 | 74.4863
CO emissions - 10% |  |  | 10 | 14.7638 | 354.9848 | 9.4 | 137.2112 | #N/A
CO emissions - 20% |  |  | 20 | 13.2496 | 544.5159 | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | 22.8972 | 629.1903 | 8.6 | 119.7584 | 79.2334
CO emissions - 30% |  |  | 30 | #N/A | 914.8985 | 8.5 | 130.2479 | #N/A
CO emissions - 40% |  |  | 40 | #N/A | #N/A | 8.3 | #N/A | 76.606
CO emissions - 50% |  |  | 50 | #N/A | #N/A | 8.1 | #N/A | #N/A
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 84.9 | 151.3698 | 143.6765
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | 84.3 | 164.7468 | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | #N/A | #N/A | 98.2 | 142.7415 | 77.9153
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | 117.1 | 145.8676 | #N/A
NOx emissions - 40% |  |  | 40 | #N/A | #N/A | 166.7 | #N/A | 84.3584
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | 195.9 | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 1.811 | 2.7068 | 19.5232 | 19.5751 | 46.488
Qtest (input) - 10% |  |  | 10 | 1.7853 | 2.5916 | 19.3573 | 19.8289 | #N/A
Qtest (input) - 20% |  |  | 20 | 1.8641 | 2.5873 | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | 1.8124 | 2.6141 | 18.6949 | 19.9369 | 43.3452
Qtest (input) - 30% |  |  | 30 | #N/A | 2.6008 | 18.3353 | 19.7639 | #N/A
Qtest (input) - 40% |  |  | 40 | #N/A | #N/A | 17.9536 | #N/A | 44.9851
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | 17.6443 | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 33.9 | 37.4 | 34.48 | 32.58 | 99.8057
Flue gases temperatures - 10% |  |  | 10 | 34.7 | 36.4 | 34.45 | 32.62 | #N/A
Flue gases temperatures - 20% |  |  | 20 | 36.6 | 35.9 | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | 37.65 | 35.9 | 34.61 | 32.55 | 95.7097
Flue gases temperatures - 30% |  |  | 30 | #N/A | 35.8 | 39.55 | 32.56 | #N/A
Flue gases temperatures - 40% |  |  | 40 | #N/A | #N/A | 41.38 | #N/A | 97.9651
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | 39.69 | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 0.5 | 2.7 | 6.34 | 1.45 | 7.6761
CO2 emissions - 10% |  |  | 10 | 0.5 | 2.6 | 6.14 | 1.46 | #N/A
CO2 emissions - 20% |  |  | 20 | 0.5 | 2.5 | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | 0.45 | 2.5 | 5.71 | 1.33 | 6.6486
CO2 emissions - 30% |  |  | 30 | #N/A | 2.4 | 5.46 | 1.3 | #N/A
CO2 emissions - 40% |  |  | 40 | #N/A | #N/A | 5.11 | #N/A | 5.8582
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | 4.76 | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | 20 | #N/A | 9.17 | 18.14 | 7.3253
O2 emissions - 10% |  |  | 10 | 19.97 | #N/A | 9.24 | 18.17 | #N/A
O2 emissions - 20% |  |  | 20 | 19.95 | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | 19.93 | #N/A | 9.58 | 18.21 | 8.5371
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | 9.76 | 18.22 | #N/A
O2 emissions - 40% |  |  | 40 | #N/A | #N/A | 9.95 | #N/A | 9.2798
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | 10.04 | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 21 | #N/A | 1.7751 | 7.3427 | 1.5357
Air Excess (Lambda) - 10% |  |  | 10 | 20.3883 | #N/A | 1.7857 | 7.4205 | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | 20 | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | 19.6262 | #N/A | 1.8389 | 7.5269 | 1.685
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | 1.8683 | 7.554 | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | #N/A | #N/A | 1.9005 | #N/A | 1.7918
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | 1.9161 | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
Qmin
|  | H2 | % | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 0% |  | %H2 in test gas | 0 | #N/A | 40 | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | 40 | 10 | 10.113 | #N/A
H2 - 20% |  |  | 20 | #N/A | 40 | #N/A | 23.0576 | #N/A
H2 - 23% |  |  | 23 | #N/A | 40 | 23 | #N/A | 21.2708
H2 - 30% |  |  | 30 | #N/A | 40 | 30 | #N/A | #N/A
H2 - 40% |  |  | 40 | #N/A | 40 | 40 | #N/A | 38.2725
H2 - 50% |  |  | 50 | #N/A | 40 | 50 | #N/A | #N/A
H2 - 60% |  |  | 60 | #N/A | 40 | #N/A | #N/A | #N/A
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | #N/A | 45.7145 | 50.6063 | 50.6063 | 50.6063
Wobbe index - 10% |  |  | 10 | #N/A | 45.7145 | 49.3664 | 49.3648 | #N/A
Wobbe index - 20% |  |  | 20 | #N/A | 45.7145 | #N/A | 47.7705 | #N/A
Wobbe index - 23% |  |  | 23 | #N/A | 45.7145 | 47.7899 | #N/A | 47.9903
Wobbe index - 30% |  |  | 30 | #N/A | 45.7145 | 46.92 | #N/A | #N/A
Wobbe index - 40% |  |  | 40 | #N/A | 45.7145 | 45.7263 | #N/A | 45.9198
Wobbe index - 50% |  |  | 50 | #N/A | 45.7145 | 44.5802 | #N/A | #N/A
Wobbe index - 60% |  |  | 60 | #N/A | 45.7145 | #N/A | #N/A | #N/A
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 72.4 | 79.3506 | #N/A
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | 74.3 | 79.2258 | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | 81.1701 | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | #N/A | 74.7 | #N/A | #N/A
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | 73.2 | #N/A | #N/A
Efficiency (Hi) - 40% |  |  | 40 | #N/A | #N/A | 71.6 | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | 70 | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 8.5 | 425.783 | 31.0101
CO emissions - 10% |  |  | 10 | #N/A | #N/A | 8.9 | 855.8062 | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 691.3865 | #N/A
CO emissions - 23% |  |  | 23 | #N/A | #N/A | 9.4 | #N/A | 37.1516
CO emissions - 30% |  |  | 30 | #N/A | #N/A | 9.3 | #N/A | #N/A
CO emissions - 40% |  |  | 40 | #N/A | #N/A | 9.1 | #N/A | 37.2017
CO emissions - 50% |  |  | 50 | #N/A | #N/A | 8.9 | #N/A | #N/A
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 84.6 | 117.4627 | 112.2594
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | 85.1 | 39.6018 | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 81.257 | #N/A
NOx emissions - 23% |  |  | 23 | #N/A | #N/A | 79.3 | #N/A | 65.5846
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | 89.4 | #N/A | #N/A
NOx emissions - 40% |  |  | 40 | #N/A | #N/A | 113.9 | #N/A | 44.7857
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | 130.4 | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 9.7145 | 11.6655 | 27.3009
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | 9.6421 | 11.4905 | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | 11.3879 | #N/A
Qtest (input) - 23% |  |  | 23 | #N/A | #N/A | 9.4266 | #N/A | 27.0409
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | 9.3167 | #N/A | #N/A
Qtest (input) - 40% |  |  | 40 | #N/A | #N/A | 9.1808 | #N/A | 25.6543
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | 9.0373 | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 32.66 | 34.88 | 81.892
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | 32.63 | 34.64 | #N/A
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | 36.06 | #N/A
Flue gases temperatures - 23% |  |  | 23 | #N/A | #N/A | 32.73 | #N/A | 82.2495
Flue gases temperatures - 30% |  |  | 30 | #N/A | #N/A | 34 | #N/A | #N/A
Flue gases temperatures - 40% |  |  | 40 | #N/A | #N/A | 37.61 | #N/A | 80.752
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | 39.83 | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 6.63 | 0.75 | 7.9439
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | 6.33 | 0.78 | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 0.7 | #N/A
CO2 emissions - 23% |  |  | 23 | #N/A | #N/A | 5.85 | #N/A | 6.7761
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | 5.62 | #N/A | #N/A
CO2 emissions - 40% |  |  | 40 | #N/A | #N/A | 5.27 | #N/A | 5.8473
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | 4.9 | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 8.86 | 19.26 | 6.3841
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | 9.1 | 19.35 | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | 19.42 | #N/A
O2 emissions - 23% |  |  | 23 | #N/A | #N/A | 9.5 | #N/A | 7.8689
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | 9.65 | #N/A | #N/A
O2 emissions - 40% |  |  | 40 | #N/A | #N/A | 9.8 | #N/A | 8.9198
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | 10.02 | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 1.7298 | 12.069 | 1.4368
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | 1.7647 | 12.7273 | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | 13.2911 | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | #N/A | #N/A | 1.8261 | #N/A | 1.5993
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | 1.8502 | #N/A | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | #N/A | #N/A | 1.875 | #N/A | 1.7384
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | 1.9126 | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A

## Seg700 Heat Pumps
Do not touch this colum | THyGA Segment 700 - Heat Pumps |  |  | THyGA Test data - Values | Graph for the indicator (KPI): |  |  | Unburnt H2 emissions
|  |  |  | GA14 |  | GA14
| SEGMENT Nr |  |  | GA14_SEGM_703
|  | Report test lab code |  | 703 | Qmax | Graph title | THyGA Segment 700 - Heat Pumps - Unburnt H2 emissions at Qmax |  | Y axis | Unburnt (ppm)
|  | Appliance type code (B, CH, CO, F, WH,O) (*) |  | GA14 | %H2 | GA14
|  | Appliance type |  | O | 0 | 5.2623
[5 empty] | 10 | #N/A
|  | Burner type |  | premix | 20 | #N/A
|  | For cooker hobs: burner tested? |  | na | 23 | #N/A
|  | Modulating burner (Y/N) |  | y | 30 | #N/A
|  | Pressure regulator (Y/N) |  | y | 40 | #N/A
|  | Can the appliance be adjusted (Y/N) |  | N | 50 | #N/A
|  | Is the appliance equiped with a combustion control (Y/N) |  | N | 60 | #N/A
|  | If the appliance can be adjusted. Instructions: |  | N
|  | If Yes what technology is used? |  | N
|  | Max. power input (net) [kW] |  | 11.2 | Qmin | Graph title | THyGA Segment 700 - Heat Pumps - Unburnt H2 emissions at Qmin |  | Y axis | Unburnt (ppm)
|  | Min. power input (net) [kW] |  | 6 | %H2 | GA14
|  | Flue type |  | B23P | 0 | #N/A
|  | Flue lenght |  | 1m | 10 | #N/A
|  | Applicable standard(s) |  | EN12309 | 20 | #N/A
|  | Gas category |  | I2E(S) | 23 | #N/A
|  | Origin of the appliance |  | already used for another project | 30 | #N/A
|  | Manufacture year |  | 2021 | 40 | #N/A
[5 empty] | 50 | #N/A
[5 empty] | 60 | #N/A
QMAX
H2
H2 - 0% |  | %H2 in test gas | 0 | #N/A
H2 - 10% |  |  | 10 | #N/A
H2 - 20% |  |  | 20 | 20
H2 - 23% |  |  | 23 | 23
H2 - 30% |  |  | 30 | 30
H2 - 40% |  |  | 40 | 40
H2 - 50% |  |  | 50 | #N/A
H2 - 60% |  |  | 60 | #N/A
|  | Wobbe index | [MJ/m³] | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6063
Wobbe index - 10% |  |  | 10 | #N/A
Wobbe index - 20% |  |  | 20 | 48.1467
Wobbe index - 23% |  |  | 23 | 47.7776
Wobbe index - 30% |  |  | 30 | 46.92
Wobbe index - 40% |  |  | 40 | 45.7145
Wobbe index - 50% |  |  | 50 | #N/A
Wobbe index - 60% |  |  | 60 | #N/A
|  | Efficiency (Hi) | % on Hi | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 151.1874
Efficiency (Hi) - 10% |  |  | 10 | #N/A
Efficiency (Hi) - 20% |  |  | 20 | 150.9566
Efficiency (Hi) - 23% |  |  | 23 | 153.7033
Efficiency (Hi) - 30% |  |  | 30 | 151.151
Efficiency (Hi) - 40% |  |  | 40 | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A
|  | CO emissions | ppm | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 159.2168
CO emissions - 10% |  |  | 10 | #N/A
CO emissions - 20% |  |  | 20 | 78.008
CO emissions - 23% |  |  | 23 | 70.5602
CO emissions - 30% |  |  | 30 | 64.9111
CO emissions - 40% |  |  | 40 | 36.244
CO emissions - 50% |  |  | 50 | #N/A
CO emissions - 60% |  |  | 60 | #N/A
|  | NOx emissions | ppm | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | 36.5972
NOx emissions - 10% |  |  | 10 | #N/A
NOx emissions - 20% |  |  | 20 | 20.5284
NOx emissions - 23% |  |  | 23 | 15.1299
NOx emissions - 30% |  |  | 30 | 13.8109
NOx emissions - 40% |  |  | 40 | 10.1483
NOx emissions - 50% |  |  | 50 | #N/A
NOx emissions - 60% |  |  | 60 | #N/A
|  | Qtest (input) | kW | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 11.4027
Qtest (input) - 10% |  |  | 10 | #N/A
Qtest (input) - 20% |  |  | 20 | 10.9349
Qtest (input) - 23% |  |  | 23 | 10.7248
Qtest (input) - 30% |  |  | 30 | 10.6211
Qtest (input) - 40% |  |  | 40 | #N/A
Qtest (input) - 50% |  |  | 50 | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A
|  | Flue gases temperatures | [°C] | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 69.38
Flue gases temperatures - 10% |  |  | 10 | #N/A
Flue gases temperatures - 20% |  |  | 20 | 68.1664
Flue gases temperatures - 23% |  |  | 23 | 61.3185
Flue gases temperatures - 30% |  |  | 30 | 62.715
Flue gases temperatures - 40% |  |  | 40 | 62.25
Flue gases temperatures - 50% |  |  | 50 | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A
|  | CO2 emissions | [%] | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 9.19
CO2 emissions - 10% |  |  | 10 | #N/A
CO2 emissions - 20% |  |  | 20 | 8.06
CO2 emissions - 23% |  |  | 23 | 7.939
CO2 emissions - 30% |  |  | 30 | 7.7
CO2 emissions - 40% |  |  | 40 | 7
CO2 emissions - 50% |  |  | 50 | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A
|  | O2 emissions | [%] | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | 4.4
O2 emissions - 10% |  |  | 10 | #N/A
O2 emissions - 20% |  |  | 20 | 5.7
O2 emissions - 23% |  |  | 23 | 5.8
O2 emissions - 30% |  |  | 30 | 5.9
O2 emissions - 40% |  |  | 40 | 6.7
O2 emissions - 50% |  |  | 50 | #N/A
O2 emissions - 60% |  |  | 60 | #N/A
|  | Unburnt UHC emissions | ppm | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | 45.3877
Unburnt UHC emissions - 23% |  |  | 23 | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A
|  | Unburnt H2 emissions | ppm | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | 5.2623
Unburnt H2 emissions - 23% |  |  | 23 | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A
|  | Air Excess (Lambda) |  | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 1.2651
Air Excess (Lambda) - 10% |  |  | 10 | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | 1.3725
Air Excess (Lambda) - 23% |  |  | 23 | 1.3816
Air Excess (Lambda) - 30% |  |  | 30 | 1.3907
Air Excess (Lambda) - 40% |  |  | 40 | 1.4685
Air Excess (Lambda) - 50% |  |  | 50 | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A
Qmin
|  | H2 | % | #N/A
H2 - 0% |  | %H2 in test gas | 0 | #N/A
H2 - 10% |  |  | 10 | 40
H2 - 20% |  |  | 20 | 20
H2 - 23% |  |  | 23 | 23
H2 - 30% |  |  | 30 | 30
H2 - 40% |  |  | 40 | 40
H2 - 50% |  |  | 50 | 40
H2 - 60% |  |  | 60 | 40
|  | Wobbe index | [MJ/m³] | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6063
Wobbe index - 10% |  |  | 10 | 45.7145
Wobbe index - 20% |  |  | 20 | 48.1467
Wobbe index - 23% |  |  | 23 | 47.7776
Wobbe index - 30% |  |  | 30 | 46.92
Wobbe index - 40% |  |  | 40 | 45.7145
Wobbe index - 50% |  |  | 50 | 45.7145
Wobbe index - 60% |  |  | 60 | 45.7145
|  | Efficiency (Hi) | % on Hi | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 118.9172
Efficiency (Hi) - 10% |  |  | 10 | #N/A
Efficiency (Hi) - 20% |  |  | 20 | 117.044
Efficiency (Hi) - 23% |  |  | 23 | 119.1505
Efficiency (Hi) - 30% |  |  | 30 | 122.8547
Efficiency (Hi) - 40% |  |  | 40 | 120.2356
Efficiency (Hi) - 50% |  |  | 50 | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A
|  | CO emissions | ppm | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 79.4051
CO emissions - 10% |  |  | 10 | #N/A
CO emissions - 20% |  |  | 20 | 33.9313
CO emissions - 23% |  |  | 23 | 34.9689
CO emissions - 30% |  |  | 30 | 26.0699
CO emissions - 40% |  |  | 40 | 17.1893
CO emissions - 50% |  |  | 50 | #N/A
CO emissions - 60% |  |  | 60 | #N/A
|  | NOx emissions | ppm | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | 32.8448
NOx emissions - 10% |  |  | 10 | #N/A
NOx emissions - 20% |  |  | 20 | 18.2216
NOx emissions - 23% |  |  | 23 | 15.5995
NOx emissions - 30% |  |  | 30 | 14.4968
NOx emissions - 40% |  |  | 40 | 9.7716
NOx emissions - 50% |  |  | 50 | #N/A
NOx emissions - 60% |  |  | 60 | #N/A
|  | Qtest (input) | kW | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 6.0232
Qtest (input) - 10% |  |  | 10 | #N/A
Qtest (input) - 20% |  |  | 20 | 5.9984
Qtest (input) - 23% |  |  | 23 | 5.9315
Qtest (input) - 30% |  |  | 30 | 5.7867
Qtest (input) - 40% |  |  | 40 | 5.6047
Qtest (input) - 50% |  |  | 50 | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A
|  | Flue gases temperatures | [°C] | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 64
Flue gases temperatures - 10% |  |  | 10 | #N/A
Flue gases temperatures - 20% |  |  | 20 | 61.6
Flue gases temperatures - 23% |  |  | 23 | 61.105
Flue gases temperatures - 30% |  |  | 30 | 62.7067
Flue gases temperatures - 40% |  |  | 40 | 62.4165
Flue gases temperatures - 50% |  |  | 50 | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A
|  | CO2 emissions | [%] | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 9.673
CO2 emissions - 10% |  |  | 10 | #N/A
CO2 emissions - 20% |  |  | 20 | 8.475
CO2 emissions - 23% |  |  | 23 | 8.4
CO2 emissions - 30% |  |  | 30 | 8.0692
CO2 emissions - 40% |  |  | 40 | 7.2699
CO2 emissions - 50% |  |  | 50 | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A
|  | O2 emissions | [%] | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | 3.5
O2 emissions - 10% |  |  | 10 | #N/A
O2 emissions - 20% |  |  | 20 | 4.9
O2 emissions - 23% |  |  | 23 | 4.8
O2 emissions - 30% |  |  | 30 | 5.1
O2 emissions - 40% |  |  | 40 | 5.9
O2 emissions - 50% |  |  | 50 | #N/A
O2 emissions - 60% |  |  | 60 | #N/A
|  | Unburnt UHC emissions | ppm | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A
|  | Unburnt H2 emissions | ppm | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A
|  | Air Excess (Lambda) |  | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 1.2
Air Excess (Lambda) - 10% |  |  | 10 | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | 1.3043
Air Excess (Lambda) - 23% |  |  | 23 | 1.2963
Air Excess (Lambda) - 30% |  |  | 30 | 1.3208
Air Excess (Lambda) - 40% |  |  | 40 | 1.3907
Air Excess (Lambda) - 50% |  |  | 50 | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A

## Seg800 Other
Do not touch this colum | THyGA Segment 800 - Other |  |  | THyGA Test data - Values | [7 empty] | Graph for the indicator (KPI): |  |  |  |  | CO emissions
|  |  |  | GA15V03 | EB12V03 | EB13V03 | EB25V02 | EB26V02 | GW24V02 | GW25V02 | GW26V02 |  | GA15V03 | EB12V03 | EB13V03 | EB25V02 | EB26V02 | GW24V02 | GW25V02 | GW26V02
| SEGMENT Nr |  |  | GA15_SEGM_809 | EB12_SEGM_803 | EB13_SEGM_802 | EB25_SEGM_802 | EB26_SEGM_802 | GW24_SEGM_805 | GW25_SEGM_806 | GW26_SEGM_807
|  | Report test lab code |  | 809 | 803 | 802 | 802 | 802 | 805 | 806 | 807 | Qmax | Graph title | THyGA Segment 800 - Other - CO emissions at Qmax | [5 empty] | Y axis | CO emissions (ppm)
|  | Appliance type code (B, CH, CO, F, WH,O) (*) |  | GA15 | EB12 | EB13 | EB25 | EB26 | GW24 | GW25 | GW26 | %H2 | GA15 | EB12 | EB13 | EB25 | EB26 | GW24 | GW25 | GW26
|  | Appliance type |  | O | O | O | EN 17175 Gas-fired overhead radiant strip heater | (O) Gas-fired overhead radiant strip heaters | O | O | O | 0 | 268.5613 | #N/A | #N/A | 5 | 43 | #N/A | 1.54 | 4.82
|  |  |  | Domestic tumble dryer | 0 | 0 | 0 | 0 |  |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.19 | 4.25
|  | Burner type |  | Atmospheric | Luminous Heater | IR - Heater | Premix + warm air recirculation | Atmospheric |  |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | For cooker hobs: burner tested? |  | na | 0 | 0 | n.a. | 0 |  |  |  | 23 | 167.9945 | 7 | #N/A | 2 | 34 | #N/A | 0.94 | 3.74
|  | Modulating burner (Y/N) |  | na | Y | Y | Y | N | Y | N | Y | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.13 | 3.19
|  | Pressure regulator (Y/N) |  | Y | Y | 0 | Y | N | Y | Y | Y | 40 | 138.3863 | #N/A | #N/A | 1 | 28 | #N/A | 1.77 | 2.83
|  | Can the appliance be adjusted (Y/N) |  | N | Y | Y | N* | N | N | N | N | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.23 | 2.49
|  | Is the appliance equiped with a combustion control (Y/N) |  | na | N | N | N | Y | N | N | N | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.46 | 2.05
|  | If the appliance can be adjusted. Instructions: |  | na | 0 | Changing of the gas type or adjusting the combustion Air and gas pressure according to the instructions in the manual | N* | 0
|  | If Yes what technology is used? |  | na | 0 | 0 | 0 | Ionization flame control
|  | Max. power input (net) [kW] |  | 4 | 15.4 | 10 | 60 | 54 | 36 | 98 | 50 | Qmin | Graph title | THyGA Segment 800 - Other - CO emissions at Qmin | [5 empty] | Y axis | CO emissions (ppm)
|  | Min. power input (net) [kW] |  | na | 11.9 | 7 | 30 | - | 22 |  | 15 | %H2 | GA15 | EB12 | EB13 | EB25 | EB26 | GW24 | GW25 | GW26
|  | Flue type |  | B22 | A1 | B53, C13, C43, C53, C63 | B22, B52, Single Wall Ø 120mm | B22 |  |  |  | 0 | #N/A | 361.0493 | 27.6961 | 1 | #N/A | 17.2 | #N/A | #N/A
|  | Flue lenght |  | 1m | 1 m | 1 m | 2m | 1 | 1m | 1m | 1m | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | 14.8 | #N/A | #N/A
|  | Applicable standard(s) |  | EN 1458-1 // EN1458-2 | EN419 | EN 416 | EN 17175 | EN 17175:2019 |  |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Gas category |  | II2H3P | II2ELL3B/P | I2E, II2ELL | II 2H3P (see attached certification) | II2H3+ |  |  |  | 23 | #N/A | 110.9889 | 4.0187 | #N/A | #N/A | 12.9 | #N/A | #N/A
|  | Origin of the appliance |  | new | 0 | Dortmund | Carlieuklima | ITALY | new | new | new | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | 12.3 | #N/A | #N/A
|  | Manufacture year |  | 2022 | 0 | 2022 | 2022 SN: CKHE593 | 2022 | 2022 | 2022 | 2022 | 40 | #N/A | 129.9388 | 1.8692 | #N/A | #N/A | 12.4 | #N/A | #N/A
|  |  |  | Domestic dryer | IR radiant heater | IR radiant heater | IR radiant heater | IR radiant heater | Air heater | Air heater | Air heater<70kW | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 13.1 | #N/A | #N/A
[12 empty] | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 11.1 | #N/A | #N/A
QMAX
H2
H2 - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 10 | 10
H2 - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 23% |  |  | 23 | 23 | 23 | 22.2 | 22.9 | 23 | #N/A | 23 | 23
H2 - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 30 | 30
H2 - 40% |  |  | 40 | 40 | 40 | 39.3 | 39.15 | 40 | #N/A | 40 | 40
H2 - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 50 | 50
H2 - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 60 | 60
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | 50.6063 | #N/A | 50.6063 | 50.6063
Wobbe index - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 49.3787 | 49.3787
Wobbe index - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 23% |  |  | 23 | 47.7776 | 47.7776 | 47.8759 | 47.7899 | 47.7776 | #N/A | 47.7776 | 47.7776
Wobbe index - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 46.92 | 46.92
Wobbe index - 40% |  |  | 40 | 45.7145 | 45.7145 | 45.7977 | 45.8155 | 45.7145 | #N/A | 45.7145 | 45.7145
Wobbe index - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 44.5578 | 44.5578
Wobbe index - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 43.4999 | 43.4999
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | 87.3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 40% |  |  | 40 | 80 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | 268.5613 | #N/A | #N/A | 5 | 43 | #N/A | 1.54 | 4.82
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.19 | 4.25
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | 167.9945 | 7 | #N/A | 2 | 34 | #N/A | 0.94 | 3.74
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.13 | 3.19
CO emissions - 40% |  |  | 40 | 138.3863 | #N/A | #N/A | 1 | 28 | #N/A | 1.77 | 2.83
CO emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.23 | 2.49
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.46 | 2.05
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | 49.2362 | #N/A | #N/A | 37.8 | 26 | #N/A | 57.9 | 39.8
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 58.1 | 30.6
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | 46.1985 | #N/A | #N/A | 18.9 | 25 | #N/A | 60.5 | 19.9
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 61 | 15
NOx emissions - 40% |  |  | 40 | 55.3545 | #N/A | #N/A | 9.45 | 30 | #N/A | 65.8 | 10.4
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 68.8 | 6.7
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 75.4 | 4.6
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | 3.7544 | 13.1264 | 9.9395 | 56.3627 | 52.6278 | #N/A | 102.0961 | 43.6113
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 98.6076 | 42.1764
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | 3.4732 | 12.1846 | 9.26 | 54.3735 | 51.5264 | #N/A | 96.3804 | 40.39
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 92.7202 | 39.503
Qtest (input) - 40% |  |  | 40 | 3.2776 | 11.2283 | 8.8655 | 49.2109 | 48.1696 | #N/A | 90.4148 | 37.9038
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 87.388 | 36.0472
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 84.6751 | 34.2971
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | 55.4 | 129.96 | 102.7422 | 108.3 | 162 | #N/A | 909 | 68.1
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 895 | 68
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | 53.6 | 144.86 | 95.7635 | 106.2 | 167.4 | #N/A | 878 | 66.8
Flue gases temperatures - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 863 | 67
Flue gases temperatures - 40% |  |  | 40 | 51.5 | 126.25 | 99.2467 | 104.2 | 168.1 | #N/A | 846 | 66.1
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 827 | 64.9
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 811 | 64.9
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | 0.26 | 10.84 | 5.9358 | 9.3 | 6.8 | #N/A | 4.19 | 8.87
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.94 | 8.36
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | 0.26 | 10.67 | 5.2314 | 8.5 | 6.5 | #N/A | 3.53 | 7.62
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.33 | 7.14
CO2 emissions - 40% |  |  | 40 | 0.22 | 9.3 | 4.2533 | 8 | 5.9 | #N/A | 3.02 | 6.49
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.67 | 5.76
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.32 | 4.97
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | 20.6 | #N/A | #N/A | 4.3 | 8.6 | #N/A | 13.47 | 4.86
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 13.74 | 5.35
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | 20.76 | #N/A | #N/A | 5.7 | 9.3 | #N/A | 14.23 | 6.11
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 14.49 | 6.6
O2 emissions - 40% |  |  | 40 | 20.79 | #N/A | #N/A | 6.7 | 10.2 | #N/A | 14.79 | 7.24
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15.23 | 7.99
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15.51 | 8.71
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 697.8336 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | 386.1237 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | 52.5 | #N/A | #N/A | 1.2575 | 1.6935 | #N/A | 2.7888 | 1.3011
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2.8926 | 1.3419
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | 87.5 | #N/A | #N/A | 1.3725 | 1.7949 | #N/A | 3.1019 | 1.4103
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.2258 | 1.4583
Air Excess (Lambda) - 40% |  |  | 40 | 100 | #N/A | #N/A | 1.4685 | 1.9444 | #N/A | 3.3816 | 1.5262
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.6395 | 1.6141
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.8251 | 1.7087
Qmin
|  | H2 | % | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
H2 - 0% |  | %H2 in test gas | 0 | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | 40 | 40
H2 - 10% |  |  | 10 | 40 | #N/A | #N/A | #N/A | #N/A | 10 | 40 | 40
H2 - 20% |  |  | 20 | 40 | #N/A | #N/A | #N/A | #N/A | 40 | 40 | 40
H2 - 23% |  |  | 23 | 40 | 23 | 22.3 | 22.9 | #N/A | 23 | 40 | 40
H2 - 30% |  |  | 30 | 40 | #N/A | #N/A | #N/A | #N/A | 30 | 40 | 40
H2 - 40% |  |  | 40 | 40 | 40 | 39.4 | 39.15 | #N/A | 40 | 40 | 40
H2 - 50% |  |  | 50 | 40 | #N/A | #N/A | #N/A | #N/A | 50 | 40 | 40
H2 - 60% |  |  | 60 | 40 | #N/A | #N/A | #N/A | #N/A | 60 | 40 | 40
|  | Wobbe index | [MJ/m³] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Wobbe index - 0% |  | %H2 in test gas | 0 | 45.7145 | 50.6063 | 50.6063 | 50.6063 | #N/A | 50.6063 | 45.7145 | 45.7145
Wobbe index - 10% |  |  | 10 | 45.7145 | #N/A | #N/A | #N/A | #N/A | 49.3787 | 45.7145 | 45.7145
Wobbe index - 20% |  |  | 20 | 45.7145 | #N/A | #N/A | #N/A | #N/A | #N/A | 45.7145 | 45.7145
Wobbe index - 23% |  |  | 23 | 45.7145 | 47.7776 | 47.8636 | 47.7899 | #N/A | 47.7776 | 45.7145 | 45.7145
Wobbe index - 30% |  |  | 30 | 45.7145 | #N/A | #N/A | #N/A | #N/A | 46.92 | 45.7145 | 45.7145
Wobbe index - 40% |  |  | 40 | 45.7145 | 45.7145 | 45.7858 | 45.8155 | #N/A | 45.7145 | 45.7145 | 45.7145
Wobbe index - 50% |  |  | 50 | 45.7145 | #N/A | #N/A | #N/A | #N/A | 44.5578 | 45.7145 | 45.7145
Wobbe index - 60% |  |  | 60 | 45.7145 | #N/A | #N/A | #N/A | #N/A | 43.4999 | 45.7145 | 45.7145
|  | Efficiency (Hi) | % on Hi | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Efficiency (Hi) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | CO emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 0% |  | %H2 in test gas | 0 | #N/A | 361.0493 | 27.6961 | 1 | #N/A | 17.2 | #N/A | #N/A
CO emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | 14.8 | #N/A | #N/A
CO emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO emissions - 23% |  |  | 23 | #N/A | 110.9889 | 4.0187 | #N/A | #N/A | 12.9 | #N/A | #N/A
CO emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | 12.3 | #N/A | #N/A
CO emissions - 40% |  |  | 40 | #N/A | 129.9388 | 1.8692 | #N/A | #N/A | 12.4 | #N/A | #N/A
CO emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 13.1 | #N/A | #N/A
CO emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 11.1 | #N/A | #N/A
|  | NOx emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | 15 | #N/A | 67.3 | #N/A | #N/A
NOx emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | 71.4 | #N/A | #N/A
NOx emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | 8.4 | #N/A | 73.8 | #N/A | #N/A
NOx emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | 75.4 | #N/A | #N/A
NOx emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | 4.2 | #N/A | 78.4 | #N/A | #N/A
NOx emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 82.5 | #N/A | #N/A
NOx emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 87.6 | #N/A | #N/A
|  | Qtest (input) | kW | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 0% |  | %H2 in test gas | 0 | #N/A | 6.7152 | 6.6755 | 34.4156 | #N/A | 22.7677 | #N/A | #N/A
Qtest (input) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | 21.676 | #N/A | #N/A
Qtest (input) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Qtest (input) - 23% |  |  | 23 | #N/A | 6.2686 | 6.1182 | 33.2705 | #N/A | 20.5235 | #N/A | #N/A
Qtest (input) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | 19.9453 | #N/A | #N/A
Qtest (input) - 40% |  |  | 40 | #N/A | 5.8157 | 5.777 | 29.558 | #N/A | 19.1387 | #N/A | #N/A
Qtest (input) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 18.3058 | #N/A | #N/A
Qtest (input) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 17.3676 | #N/A | #N/A
|  | Flue gases temperatures | [°C] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 0% |  | %H2 in test gas | 0 | #N/A | 47.08 | 98.7711 | 84.1 | #N/A | 163.9 | #N/A | #N/A
Flue gases temperatures - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | 157.8 | #N/A | #N/A
Flue gases temperatures - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Flue gases temperatures - 23% |  |  | 23 | #N/A | 48.89 | 97.3983 | 82.4 | #N/A | 152.1 | #N/A | #N/A
Flue gases temperatures - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | 149.1 | #N/A | #N/A
Flue gases temperatures - 40% |  |  | 40 | #N/A | 41.55 | 96.696 | 80.6 | #N/A | 145.6 | #N/A | #N/A
Flue gases temperatures - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 142 | #N/A | #N/A
Flue gases temperatures - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 139.1 | #N/A | #N/A
|  | CO2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | 11.54 | 5.7357 | 8.6 | #N/A | 9.5 | #N/A | #N/A
CO2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | 8.92 | #N/A | #N/A
CO2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 emissions - 23% |  |  | 23 | #N/A | 10.02 | 4.8365 | 7.9 | #N/A | 8.13 | #N/A | #N/A
CO2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | 7.64 | #N/A | #N/A
CO2 emissions - 40% |  |  | 40 | #N/A | 8.71 | 4.1512 | 7.3 | #N/A | 6.98 | #N/A | #N/A
CO2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 6.21 | #N/A | #N/A
CO2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 5.47 | #N/A | #N/A
|  | O2 emissions | [%] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | 5.6 | #N/A | 3.59 | #N/A | #N/A
O2 emissions - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | 4.21 | #N/A | #N/A
O2 emissions - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
O2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | 6.8 | #N/A | 5.02 | #N/A | #N/A
O2 emissions - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | 5.53 | #N/A | #N/A
O2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | 7.8 | #N/A | 6.15 | #N/A | #N/A
O2 emissions - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 6.9 | #N/A | #N/A
O2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 7.61 | #N/A | #N/A
|  | Unburnt UHC emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | 654.8346 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 40% |  |  | 40 | #N/A | #N/A | 346.2673 | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt UHC emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Unburnt H2 emissions | ppm | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 23% |  |  | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 40% |  |  | 40 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Unburnt H2 emissions - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Air Excess (Lambda) |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 0% |  | %H2 in test gas | 0 | #N/A | #N/A | #N/A | 1.3636 | #N/A | 1.2062 | #N/A | #N/A
Air Excess (Lambda) - 10% |  |  | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | 1.2507 | #N/A | #N/A
Air Excess (Lambda) - 20% |  |  | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Air Excess (Lambda) - 23% |  |  | 23 | #N/A | #N/A | #N/A | 1.4789 | #N/A | 1.3141 | #N/A | #N/A
Air Excess (Lambda) - 30% |  |  | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | 1.3575 | #N/A | #N/A
Air Excess (Lambda) - 40% |  |  | 40 | #N/A | #N/A | #N/A | 1.5909 | #N/A | 1.4141 | #N/A | #N/A
Air Excess (Lambda) - 50% |  |  | 50 | #N/A | #N/A | #N/A | #N/A | #N/A | 1.4894 | #N/A | #N/A
Air Excess (Lambda) - 60% |  |  | 60 | #N/A | #N/A | #N/A | #N/A | #N/A | 1.5683 | #N/A | #N/A